# [***81 FR 2111***](https://advance.lexis.com/api/document?collection=administrative-codes&id=urn:contentItem:5HVS-GY20-006W-83TG-00000-00&context=)

Vol. 81, No. 010, Friday, January 15, 2016

Proposed Rules

**Reporter**

81 FR 2111 \*

***Federal Register* > *2016* > *January* > *Friday, January 15, 2016* > *Proposed Rules* > *DEPARTMENT OF ENERGY (DOE) -- Office of Energy Efficiency and Renewable Energy***

**Title:** **Energy Conservation Program for Certain Industrial Equipment: Energy Conservation Standards for Small, Large, and Very Large Air-Cooled Commercial Package Air Conditioning and Heating Equipment and Commercial Warm Air Furnaces**

**Action:**  Supplemental notice of proposed rulemaking.

**Agency**

DEPARTMENT OF ENERGY (DOE) > Office of Energy Efficiency and Renewable Energy

**Identifier:** **[Docket Numbers EERE-2013-BT-STD-0007 and EERE-2013-BT-STD-0021]** > **RIN 1904-AC95 and 1904-AD11**

**Administrative Code Citation**

**10 CFR Part 431**

**Synopsis**

**SUMMARY:** The Energy Policy and Conservation Act of 1975, as amended (EPCA), prescribes energy conservation standards for various consumer products and certain commercial and industrial equipment, including small, large, and very large air-cooled commercial package air conditioning and heating equipment and commercial warm air furnaces. EPCA also requires that the U.S. Department of Energy (DOE) periodically review and consider amending its standards for specified categories of industrial equipment, including commercial heating and air-conditioning equipment, in order to determine whether more-stringent, amended standards would be technologically feasible and economically justified, and save a significant additional amount of energy. In this document, DOE proposes to amend the energy conservation standards for both small, large, and very large air-cooled commercial package air conditioning and heating equipment and commercial warm air furnaces identical to those set forth in a direct final rule published elsewhere in this **Federal Register** . If DOE receives an adverse comment and determines that such comment may provide a reasonable basis for withdrawing the direct final rule, DOE will publish a document withdrawing the direct final rule and will proceed with this proposed rule.

**Text**

**SUPPLEMENTARY INFORMATION:**

**Table of Contents**

I. Introduction and Authority

II. Proposed Standards

A. Benefits and Burdens of TSLs Considered for Small, Large, and Very Large Air-Cooled Commercial Package Air Conditioning and Heating Equipment

B. Benefits and Burdens of TSLs Considered for Commercial Warm Air Furnaces

III. Public Participation

A. Submission of Comments

B. Public Meeting

IV. Procedural Issues and Regulatory Review

V. Approval of the Office of the Secretary

**I. Introduction and Authority**

Title III, Part C n1 of the Energy Policy and Conservation Act of 1975 ("EPCA" or, in context, "the Act"), [*Public Law 94-163*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:5CD7-HSG0-01XN-S495-00000-00&context=) (December 22, 1975), coupled with Title IV of the National Energy Conservation Policy Act, [*Public Law 95-619*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:5CD7-HSJ0-01XN-S116-00000-00&context=) (November 9, 1978), (collectively codified at [*42 U.S.C. 6311*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GN01-NRF4-44P9-00000-00&context=)-[*6317*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GRW1-NRF4-420B-00000-00&context=)), established the Energy Conservation Program for Certain Industrial Equipment, which includes provisions covering the equipment addressed by this document. n2 In general, this program addresses the energy efficiency of certain types of commercial and industrial equipment. Relevant provisions of the Act specifically include definitions ([*42 U.S.C. 6311*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GN01-NRF4-44P9-00000-00&context=)), energy conservation standards ([*42 U.S.C. 6313*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=)), test procedures ([*42 U.S.C. 6314*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GRF1-NRF4-434F-00000-00&context=)), labeling provisions ([*42 U.S.C. 6315*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GVR1-NRF4-44M6-00000-00&context=)), and the authority to require information and reports from manufacturers ([*42 U.S.C. 6316*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GP81-NRF4-41W7-00000-00&context=)).

n1 Part C was codified as Part A-1 of the corresponding portion of the U.S. Code.

n2 All references to EPCA in this document refer to the statute as amended through the Energy Efficiency Improvement Act of 2015, *Public Law 114-11* (April 30, 2015).

Section 342(a) of EPCA, which was added as part of the Energy Policy Act of 1992, *Public Law 102-486* (October 24, 1992) ("EPAct 1992"), introduced new provisions regarding DOE's authority to regulate certain commercial and industrial equipment. Among the equipment EPAct 1992 required DOE to regulate were small and large air-cooled commercial package air conditioning and heating equipment, along with commercial warm air furnaces ("CWAFs"). See EPAct 1992, sec. 122 (codified as amended at [*42 U.S.C. 6313(a)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=)). As part of these changes, Congress specified energy conservation standards for this equipment to meet. See id. Later, the Energy Policy Act of 2005, *Public Law 109-58* (August 8, 2005) ("EPACT 2005"), further amended DOE's authority to include very large air-cooled commercial package air conditioning and heating equipment and added standards for this equipment to meet as well. See EPACT 2005, sec. 136 (codified as amended at [*42 U.S.C. 6313(a)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=)). (Small, large, and very large, air-cooled commercial package air conditioning and heating equipment are also known generally as air-cooled commercial unitary air conditioners and heat pumps ("CUACs" and "CUHPs"). Congress established standards for CUACs/CUHPs that have a rated capacity between 65,000 British thermal units per hour (Btu/h) and 760,000 Btu/h. Similarly, for CWAFs, Congress established standards for equipment that (1) have a rated capacity (rated maximum input n3) greater than or equal to 225,000 Btu/h, (2) can be gas-fired or oil-fired, and (3) are designed to heat commercial and industrial buildings. See [*42 U.S.C. 6313(a)(4)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=).

n3 "Rated maximum input" means the maximum gas-burning capacity of a CWAF in Btus per hour, as specified by the manufacturer.

Collectively, CUACs/CUHPs and CWAFs are designed to heat and cool commercial buildings and are often located on a building's rooftop.

Section 342(a) of EPCA concerns energy conservation standards for small, large, and very large, CUACs and CUHPs. ([*42 U.S.C. 6313(a)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=)) This category of equipment has a rated capacity between 65,000 Btu/h and 760,000 Btu/h. This equipment is designed to heat and cool commercial buildings and is often located on the building's rooftop.

The initial Federal energy conservation standards for CWAFs were added to EPCA by the Energy Policy Act of 1992 (EPACT 1992), *Public Law 102-486* (Oct. 24, 1992). See [*42 U.S.C. 6313(a)(4)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=). These types of covered equipment have a rated capacity (rated maximum input n4) greater than or equal to 225,000 Btu/h, can be gas-fired or oil-fired, and are designed to heat commercial and industrial buildings. *Id.*

n4 "Rated maximum input" means the maximum gas-burning capacity of a CWAF in Btus per hour, as specified by the manufacturer.

Pursuant to section 342(a)(6) of EPCA, DOE is to consider amending the energy efficiency standards for certain types of commercial and industrial equipment whenever ASHRAE amends the standard levels or design requirements prescribed in ASHRAE/IES Standard 90.1, and whenever more than 6 years had elapsed since the issuance of the most recent final rule establishing or amending a standard for the equipment as of the date of AEMTCA's enactment, December 18, 2012. ([*42 U.S.C. 6313(a)(6)(C)(vi)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=)) Because more than six years had elapsed since DOE issued a final rule with standards for CUACs and CUHPs or CWAFs on October 18, 2005 (see [*70 FR 60407),*](https://advance.lexis.com/api/document?collection=administrative-codes&id=urn:contentItem:4HBY-PT50-006W-81G4-00000-00&context=) DOE initiated the process to review these standards.

Pursuant to EPCA, DOE's energy conservation program for covered equipment consists essentially of four parts: (1) Testing; (2) labeling; (3) the establishment of Federal energy conservation standards; and (4) certification and enforcement procedures. Subject to certain criteria and conditions, DOE is required to develop test procedures to measure the energy efficiency, energy use, or estimated annual operating cost of covered equipment. ([*42 U.S.C. 6314*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GRF1-NRF4-434F-00000-00&context=)) Manufacturers of covered equipment must use the prescribed DOE test procedure as the basis for certifying to DOE that their equipment comply with the applicable energy conservation standards adopted under EPCA and when making representations to the public regarding their energy use or efficiency. ([*42 U.S.C. 6314(d)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GRF1-NRF4-434F-00000-00&context=)) Similarly, DOE must use these test procedures to determine whether a given manufacturer's equipment complies with standards adopted pursuant to EPCA. The DOE test procedures for small, large, and very large CUACs/CUHPs and CWAFs currently appear at title 10 of the Code of Federal ***Regulations*** ("CFR") 431.96 and 431.76, respectively.

When setting standards for the equipment addressed by this document, EPCA prescribes that in deciding whether a proposed standard is economically justified, DOE must determine whether the benefits of the standard exceed its burdens. DOE must make this determination after receiving comments on the proposed standard, and by considering, to the maximum extent practicable, the following seven statutory factors:

1. The economic impact of the standard on manufacturers and consumers of products subject to the standard;

2. The savings in operating costs throughout the estimated average life of the covered products in the type (or class) compared to any increase in the price, initial charges, or maintenance expenses for the covered products **[\*2113]** which are likely to result from the standard;

3. The total projected amount of energy savings likely to result directly from the standard;

4. Any lessening of the utility or the performance of the covered products likely to result from the standard;

5. The impact of any lessening of ***competition***, as determined in writing by the Attorney General, that is likely to result from the standard;

6. The need for national energy conservation; and

7. Other factors the Secretary of Energy considers relevant. ([*42 U.S.C. 6313(a)(6)(B)(ii)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=))

With respect to the types of equipment at issue in this document, EPCA also contains what is known as an "anti-backsliding" provision, which prevents the Secretary from prescribing any amended standard that either increases the maximum allowable energy use or decreases the minimum required energy efficiency of a covered product. ([*42 U.S.C. 6313(a)(6)(B)(iii)(I)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=)) Also, the Secretary may not prescribe an amended or new standard if interested persons have established by a preponderance of the evidence that the standard is likely to result in the unavailability in the United States of any covered product type (or class) of performance characteristics (including reliability, features, sizes, capacities, and volumes) that are substantially the same as those generally available in the United States. ([*42 U.S.C. 6313(a)(6)(B)(iii)(II)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=))(aa)

With respect to the equipment addressed by this document, DOE notes that EPCA prescribes limits on the Agency's ability to promulgate a standard if DOE has made a finding that interested persons have established by a preponderance of the evidence that a standard is likely to result in the unavailability of any product type (or class) of performance characteristics that are substantially the same as those generally available in the United States at the time of the finding. See [*42 U.S.C. 6313(B)(iii)(II)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=).

Additionally, EPCA generally specifies criteria to follow when promulgating multiple energy conservation standards for covered products based on different subcategories. In these cases, DOE must specify a different standard level for a type or class of product that has the same function or intended use if DOE determines that products within such group: (A) Consume a different kind of energy from that consumed by other covered products within such type (or class); or (B) have a capacity or other performance-related feature which other products within such type (or class) do not have and such feature justifies a higher or lower standard. See [*42 U.S.C. 6295(q)(1)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=). In determining whether a performance-related feature justifies a different standard for a group of products, DOE must consider such factors as the utility to the customer of such a feature and other factors DOE deems appropriate. Id. Any rule prescribing such a standard must include an explanation of the basis on which such higher or lower level was established. See [*42 U.S.C. 6295(q)(2)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=). With respect to the equipment addressed by this supplemental notice of proposed rulemaking ("SNOPR"), DOE notes that EPCA prescribes limits on the Agency's ability to promulgate a standard if DOE has made a finding that interested persons have established by a preponderance of the evidence that a standard is likely to result in the unavailability of any product type (or class) of performance characteristics that are substantially the same as those generally available in the United States at the time of the finding. See [*42 U.S.C. 6313(B)(iii)(II)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=).

With particular regard to this document, the Energy Independence and Security Act of 2007 ("EISA 2007"), *Public Law 110-140* (December 19, 2007), amended EPCA, in relevant part, to grant DOE authority to issue a type of final rule (*i.e.,* a "direct final rule") establishing an energy conservation standard for a product on receipt of a statement that is submitted jointly by interested persons that are fairly representative of relevant points of view (including representatives of manufacturers of covered products, States, and efficiency advocates), as determined by the Secretary, and that contains recommendations with respect to an energy or water conservation standard. If the Secretary determines that the recommended standard contained in the statement is in accordance with [*42 U.S.C. 6295(o)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=) or [*42 U.S.C. 6313(a)(6)(B)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=), as applicable, the Secretary may issue a final rule establishing the recommended standard. A notice of proposed rulemaking ("NOPR") that proposes an identical energy efficiency standard is published simultaneously with the direct final rule. A public comment period of at least 110 days is provided. See [*42 U.S.C. 6295(p)(4)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=). Not later than 120 days after the date on which a direct final rule issued under this authority is published in the **Federal Register**, the Secretary shall withdraw the direct final rule if the Secretary receives 1 or more adverse public comments relating to the direct final rule or any alternative joint recommendation and based on the rulemaking record relating to the direct final rule, the Secretary determines that such adverse public comments or alternative joint recommendation may provide a reasonable basis for withdrawing the direct final rule under subsection [*42 U.S.C. 6295(o)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=), [*6313(a)(6)(B)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=), or any other applicable law. On withdrawal of a direct final rule, the Secretary shall proceed with the notice of proposed rulemaking published simultaneously with the direct final rule and publish in the **Federal Register** the reasons why the direct final rule was withdrawn. This direct final rule provision applies to the equipment at issue in this SNOPR. See [*42 U.S.C. 6316(b)(1)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GP81-NRF4-41W7-00000-00&context=). In this instance, because DOE has already published NOPRs related to the amendment of standards both CUACs/CUHPs and CWAFs, see [*79 FR 58948*](https://advance.lexis.com/api/document?collection=administrative-codes&id=urn:contentItem:5D83-0X60-006W-8059-00000-00&context=) (September 30, 2014) (CUAC/CUHP proposal) and [*80 FR 6182*](https://advance.lexis.com/api/document?collection=administrative-codes&id=urn:contentItem:5F75-DKC0-006W-8215-00000-00&context=) (February 4, 2015), DOE is publishing an SNOPR consistent with the direct final rule's statutory requirements.

Responding to comments received from interested parties with respect to DOE's proposals, on April 1, 2015, DOE issued a Notice of Intent to Establish the Commercial Package Air Conditioners and Commercial Warm Air Furnaces Working Group to Negotiate Potential Energy Conservation Standards for Commercial Package Air Conditioners and Commercial Warm Air Furnaces. [*80 FR 17363.*](https://advance.lexis.com/api/document?collection=administrative-codes&id=urn:contentItem:5FN3-W590-006W-835M-00000-00&context=) The CUAC/CUHP-CWAF Working Group (in context, "the Working Group") was established under the Appliance Standards and Rulemaking Federal Advisory Committee ("ASRAC") in accordance with the Federal Advisory Committee Act and the Negotiated Rulemaking Act with the purpose of discussing and, if possible, reaching consensus on a set of energy conservation standards to propose or finalize for CUACs, CUHPs and CWAFs. The Working Group was to consist of fairly representative parties having a defined stake in the outcome of the proposed standards, and would consult, as appropriate, with a range of experts on technical issues.

DOE received 17 nominations for membership. Ultimately, the Working Group consisted of 17 members, including one member from ASRAC and one DOE representative. n5 The Working **[\*2114]** Group met six times (five times in-person and once by teleconference). The meetings were held on April 28, May 11-12, May 20-21, June 1-2, June 9-10, and June 15, 2015. As a result of these efforts, the Working Group successfully reached consensus on energy conservation standards for CUACs, CUHPs, and CWAFs. On June 15, 2015, it submitted a Term Sheet to ASRAC outlining its recommendations, which ASRAC subsequently adopted. n6 See [*http://www.****regulations****.gov/#!documentDetail*](http://www.regulations.gov/#!documentDetail)*;D=EERE-2013-BT-STD-0007-0093.*

n5 The group members were John Cymbalsky (U.S. Department of Energy), Marshall Hunt (Pacific Gas & Electric Company, San Diego Gas & Electric Company, Southern California Edison, and Southern California Gas Company), Andrew deLaski (Appliance Standards Awareness Project), Louis Starr (Northwest Energy Efficiency Alliance), Meg Waltner (Natural Resources Defense Council), Jill Hootman (Ingersoll Rand/Trane), John Hurst (Lennox), Karen Meyers (Rheem Manufacturing Company), Charlie McCrudden (Air Conditioning Contractors of America), Harvey Sachs (American Council for an Energy Efficient Economy), Paul Doppel (Mitsubishi Electric), Robert Whitwell (United Technologies Corporation), Michael Shows (Underwriters Laboratories), Russell Tharp (Goodman Manufacturing), Sami Zendah (Emerson Climate Technologies), Mark Tezigni (Sheet Metal and Air Conditioning Contractors National Association, Inc.), Nick Mislak (Air-Conditioning, Heating, and Refrigeration Institute).

n6 Available at [*http://www.****regulations****.gov/#!documentDetail*](http://www.regulations.gov/#!documentDetail)*;D=EERE-2013-BT-STD-0007-0093.* The following individuals served as members of ASRAC that received and approved the Term Sheet: Co-Chair John Mandyck (Carrier/United Technologies Corporation), Co-Chair Andrew deLaski (Appliance Standards Awareness Project), Ashley Armstrong (U.S. Department of Energy), John Caskey (National Electrical Manufacturers Association), Jennifer Cleary (Association of Home Appliance Manufacturers), Thomas Eckman (Northwest Power and Conservation Council), Charles Hon (True Manufacturing Company), Dr. David Hungerford (California Energy Commission), Dr. Diane Jakobs (Rheem Manufacturing Company), Kelley Kline (General Electric, Appliances), Deborah Miller (National Association of State Energy Officials), and Scott Blake Harris (Harris, Wiltshire & Grannis, LLP).

DOE has determined that the statement containing recommendations with respect to energy conservation standards for CUACs, CUHPs and CWAFs was submitted jointly by interested persons that are fairly representative of relevant points of view, in accordance with [*42 U.S.C. 6295(p)(4)(A)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=) and [*6313(a)(6)(B)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=). n7 In reaching this determination, DOE took into consideration the fact that the Working Group, in conjunction with ASRAC members who approved the recommendations, consisted of representatives of manufacturers of covered products, States, and efficiency advocates--all of which are groups specifically identified by Congress as relevant parties to any consensus recommendation. ([*42 U.S.C. 6295(p)(4)(A)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=) As delineated above, the Term Sheet was signed and submitted by a broad cross-section of interests, including the manufacturers of the subject equipment, trade associations representing these manufacturers and installation contractors, environmental and energy-efficiency advocacy organizations, and electric utility companies. The ASRAC Committee approving the Working Group's recommendations included at least two members representing States--one representing the National Association of State Energy Officials (NASEO) and one representing the State of California. n8 By its plain terms, the statute contemplates that the Secretary will exercise discetion to determine whether a given statement is "submitted jointly by interested persons that are fairly representative of relevant points of view (including representatives of manufacturers of covered products, States, and efficiency advocates)." In this case, given the broad range of persons participating in the process that led to the submission--in the Working Group and in ASRAC--and given the breadth of perspectives expressed in that process, DOE has determined that the statement it received meets this criterion.

n7 See [*42 U.S.C. 6313(b)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=) (applying [*42 U.S.C. 6295(p)(4)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=) to energy conservation standard rulemakings involving a variety of industrial equipment, including CUACs, CUHPs, and CWAFs).

n8 These individuals were Deborah E. Miller (NASEO) and David Hungerford (California Energy Commission).

Pursuant to [*42 U.S.C. 6295(p)(4)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=), the Secretary must also determine whether a jointly-submitted recommendation for an energy or water conservation standard satisfies [*42 U.S.C. 6295(o)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GR61-NRF4-40BK-00000-00&context=) or [*42 U.S.C. 6313(a)(6)(B)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=), as applicable. In making this determination, DOE has conducted an analysis to evaluate whether the potential energy conservation standards under consideration would meet these requirements. This evaluation is similar to the comprehensive approach that DOE typically conducts whenever it considers potential energy conservation standards for a given type of product or equipment. DOE applies the same principles to any consensus recommendations it may receive to satisfy its statutory obligation to ensure that any energy conservation standard that it adopts achieves the maximum improvement in energy efficiency that is technologically feasible and economically justified and will result in the significant conservation of energy. Upon review, the Secretary determined that the Term Sheet submitted in the instant rulemaking comports with the standard-setting criteria set forth under [*42 U.S.C. 6313(a)(6)(B)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=). As a result, DOE published a direct final rule establishing energy conservation standards for CUACs/CUHPs and CWAFs elsewhere in this **Federal Register** If DOE receives adverse comments that may provide a reasonable basis for withdrawal and withdraws the direct final rule, DOE will consider those comments and any other comments received in determining how to proceed with this proposed rule.

For further background information on these proposed standards and the supporting analyses, please see the direct final rule published elsewhere in this **Federal Register** That document includes additional discussion of the EPCA requirements for promulgation of energy conservation standards; the current standards for CUACs/CUHPs and CWAFs; the history of the standards rulemakings establishing such standards; and information on the test procedures used to measure the energy efficiency of CUACs/CUHPs and CWAFs. The document also contains an in-depth discussion of the analyses conducted in support of this rulemaking, the methodologies DOE used in conducting those analyses, and the analytical results.

**II. Proposed Standards**

When considering more stringent standards for the equipment at issue, DOE must determine, supported by clear and convincing evidence that adopting those standards would result in the significant additional conservation of energy and be technologically feasible and economically justified. See [*42 U.S.C. 6313(a)(6)(A)(ii)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=). In determining whether a standard is economically justified, the Secretary must determine whether the benefits of the standard exceed its burdens by, to the greatest extent practicable, considering the seven statutory factors discussed previously. ([*42 U.S.C. 6313(a)(6)(B)(ii)(I)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=)-(VII))

DOE considered the impacts of amended standards for CUACs/CUHPs and CWAFs at each TSL, beginning with the maximum technologically feasible level, to determine whether that level would be economically justified. Where the max-tech level was not justified, DOE then considered the next most efficient level and undertook the same evaluation until it reached the highest efficiency level that is both technologically feasible and economically justified and saves a significant amount of energy.

To aid the reader as DOE discusses the benefits and/or burdens of each TSL, tables in this section present a summary of the results of DOE's quantitative analysis for each TSL. In addition to the quantitative results presented in the tables, DOE also considers other burdens and benefits that affect economic justification. **[\*2115]**

*A. Benefits and Burdens of TSLs Considered for Small, Large, and Very Large Air-Cooled Commercial Package Air Conditioning and Heating Equipment*

Table II.1 and Table II.2 summarize the quantitative impacts estimated for each TSL for CUACs and CUHPs. The national impacts are measured over the lifetime of CUACs and CUHPs purchased in the 2018-2048 period. The energy savings, emissions reductions, and value of emissions reductions refer to full-fuel-cycle results. The efficiency levels contained in each TSL are described in section V.A of the direct final rule.

| **Table II.1--Summary of Analytical Results for Small, Large, and Very Large** | | | | | | | | |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Air-Cooled Commercial Package Air Conditioning and Heating Equipment:** | | | | | | | | |
| **National Impacts** | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
| **Category** | **TSL 1** | **TSL 2** | **TSL 2.5** | **Recom-** | **TSL 3** | **TSL 3.5** | **TSL 4** | **TSL 5** |
|  |  |  |  | **mended** |  |  |  |  |
|  |  |  |  | **TSL \*** |  |  |  |  |
| National FFC Energy Savings (quads) | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
|  | 5.3 | 9.8 | 13.9 | 14.8 | 15.9 | 16.4 | 19.7 | 23.4 |
|  |  |  |  |  |  |  |  |  |
| NPV of Consumer Benefits (2014 $ billion) | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
| 3% discount | 18.0 | 32.8 | 47.5 | 50.0 | 53.7 | 55.3 | 64.1 | 68.2 |
| rate |  |  |  |  |  |  |  |  |
| 7% discount | 5.4 | 10.1 | 15.1 | 15.2 | 16.8 | 17.1 | 19.2 | 18.8 |
| rate |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
| Cumulative Emissions Reduction (Total FFC Emissions) | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
| CO[2] | 314 | 578 | 824 | 873 | 943 | 973 | 1,167 | 1,383 |
| (million |  |  |  |  |  |  |  |  |
| metric tons) |  |  |  |  |  |  |  |  |
| SO[2] | 164 | 303 | 431 | 454 | 493 | 508 | 610 | 722 |
| (thousand |  |  |  |  |  |  |  |  |
| tons) |  |  |  |  |  |  |  |  |
| NO[X] | 586 | 1,080 | 1,538 | 1,634 | 1,759 | 1,815 | 2,180 | 2,584 |
| (thousand |  |  |  |  |  |  |  |  |
| tons) |  |  |  |  |  |  |  |  |
| Hg (tons) | 0.61 | 1.12 | 1.59 | 1.68 | 1.82 | 1.88 | 2.25 | 2.66 |
| CH[4] | 1,401 | 2,582 | 3,677 | 3,917 | 4,208 | 4,342 | 5,215 | 6,185 |
| (thousand |  |  |  |  |  |  |  |  |
| tons) |  |  |  |  |  |  |  |  |
| N[2] O | 3.45 | 6.35 | 9.05 | 9.54 | 10.34 | 10.67 | 12.80 | 15.16 |
| (thousand |  |  |  |  |  |  |  |  |
| tons) |  |  |  |  |  |  |  |  |
| CH[4] | 39.2 | 72.3 | 103.0 | 109.7 | 117.8 | 121.6 | 146.0 | 173.2 |
| (million tons |  |  |  |  |  |  |  |  |
| CO[2] eq\*\*) |  |  |  |  |  |  |  |  |
| N[2] O | 913 | 1,682 | 2,397 | 2,528 | 2,741 | 2,828 | 3,392 | 4,017 |
| (thousand |  |  |  |  |  |  |  |  |
| tons CO [2] |  |  |  |  |  |  |  |  |
| eq \* \*) |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
| Value of Emissions Reduction (Total FFC Emissions)$ | | | | | | | | |
| CO[2] | 1.845 | 3.409 | 4.870 | 5.046 | 5.556 | 5.729 | 6.860 | 8.127 |
| (2014$ | to | to | to | to | to | to | to | to |
| billion)+ | 27.53 | 50.82 | 72.52 | 75.94 | 82.83 | 85.44 | 102.4 | 121.4 |
| NO[X] --3% | 1,828 | 3,376 | 4,820 | 5,038 | 5,503 | 5,677 | 6,804 | 8,067 |
| discount rate |  |  |  |  |  |  |  |  |
| (2014$ |  |  |  |  |  |  |  |  |
| million) |  |  |  |  |  |  |  |  |
| NO[X] --7% | 606 | 1,121 | 1,604 | 1,614 | 1,826 | 1,881 | 2,245 | 2,652 |
| discount rate |  |  |  |  |  |  |  |  |
| (2014$ |  |  |  |  |  |  |  |  |
| million) |  |  |  |  |  |  |  |  |

\* For the Recommended TSL, the NES is forecasted over the lifetime of equipment sold from 2018-2048. For the other TSLs, the NES is forecasted over the lifetime of equipment sold from 2019-2048.

\* \* CO[2] eq is the quantity of CO[2] that would have the same global warming potential (GWP).

+ Range of the economic value of CO[2] reductions is based on estimates of the global benefit of reduced CO[2] emissions.

| **Table II.2--Summary of Analytical Results for Small, Large, and Very Large** | | | | | | | | |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Air-Cooled Commercial Package Air Conditioning and Heating Equipment:** | | | | | | | | |
| **Manufacturer and Consumer Impacts** | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
| **Category** | **TSL 1** | **TSL 2** | **TSL 2.5** | **Recomme** | **TSL 3** | **TSL 3.5** | **TSL 4** | **TSL 5** |
|  |  |  |  | **nded** |  |  |  |  |
|  |  |  |  | **TSL** |  |  |  |  |
| Manufacturer Impacts | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
| Industry NPV | 1,431.0 | 1,421.9 | 1,300.5 | 1,204.1 | 1,197.4 | 1,138.2 | 1,025.0 | 762.7 |
| (2014$ | to | to | to | to | to | to | to | to |
| million) (No- | 1,705.5 | 1,758.6 | 1,721.1 | 1,606.1 | 1,697.0 | 1,670.3 | 1,660.9 | 1,737.6 |
| new-standards |  |  |  |  |  |  |  |  |
| case INPV = |  |  |  |  |  |  |  |  |
| 1,638.2) |  |  |  |  |  |  |  |  |
| Industry NPV | (6.5) | (13.5) | (20.9) | (26.8) | (27.2) | (30.8) | (37.7) | (53.6) |
| (% change) | to 3.7 | to 6.9 | to 4.7 | to | to 3.2 | to 1.6 | to 1.0 | to 5.7 |
|  |  |  |  |  |  |  |  |  |
| Commercial Consumer Average LCC Savings (2014] | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
| Small CUACs | (210) | 870 | 3,777 | 4,233 | 4,233 | 3,517 | 3,035 | 5,326 |
| Large CUACs | 3,997 | 3,728 | 7,991 | 10,135 | 10,135 | 12,266 | 16,803 | 12,900 |
| Very Large | 1,547 | 4,777 | 8,610 | 8,610 | 8,881 | 8,881 | 18,386 | 18,338 |
| CUACs |  |  |  |  |  |  |  |  |
| Average \* | 1,045 | 1,971 | 5,340 | 6,220 | 6,238 | 6,396 | 8,370 | 8,697 |
|  |  |  |  |  |  |  |  |  |
| Commercial Consumer PBP (years) | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
| Small CUACs | 14.9 | 8.5 | 4.9 | 4.9 | 4.9 | 2.6 | 2.5 | 4.6 |
| Large CUACs | 1.3 | 2.4 | 2.4 | 2.6 | 2.6 | 2.6 | 2.5 | 4.6 |
| Very Large | 5.8 | 7.0 | 6.2 | 6.2 | 7.2 | 7.2 | 5.6 | 6.3 |
| CUACs |  |  |  |  |  |  |  |  |
| Average \* | 10.6 | 6.7 | 4.3 | 4.4 | 4.5 | 3.0 | 2.8 | 4.8 |
|  |  |  |  |  |  |  |  |  |
| % of Consumers that Experience Net Cost | | | | | | | | |
|  |  |  |  |  |  |  |  |  |
| Small CUACs | 48 | 25 | 5 | 5 | 5 | 13 | 25 | 16 |
| Large CUACs | 0 | 10 | 5 | 2 | 2 | 1 | 1 | 11 |
| Very Large | 7 | 13 | 7 | 7 | 23 | 23 | 3 | 6 |
| CUACs |  |  |  |  |  |  |  |  |
| Average \* | 32 | 20 | 5 | 4 | 6 | 11 | 16 | 14 |

Parentheses indicate negative (-) values.

\* Weighted by shares of each equipment class in total projected shipments in the year of compliance.

DOE first considered TSL 5, which represents the max-tech efficiency levels. TSL 5 would save 23.4 quads of energy, an amount DOE considers significant. Under TSL 5, the NPV of consumer benefit would be $ 18.8 billion using a discount rate of 7-percent, and $ 68.2 billion using a discount rate of 3-percent.

The cumulative emissions reductions at TSL 5 are 1,383 million Mt of CO[2], 722 thousand tons of SO[2], 2,584 thousand tons of NO[X], 2.66 tons of Hg, 6,185 thousand tons of CH[4,] and 15.16 thousand tons of N[2] O. The estimated monetary value of the CO[2] emissions reduction at TSL 5 ranges from $ 8.127 billion to $ 121.4 billion.

At TSL 5, the average LCC impact is a savings of $ 5,326 for small CUACs, $ 12,900 for large CUACs, and $ 18,338 for very large CUACs. The simple payback period is 4.6 years for small CUACs, 4.6 years for large CUACs, and 6.3 years for very large CUACs. The fraction of consumers experiencing a net LCC cost is 16 percent for small CUACs, 11 percent for large CUACs, and 6 percent for very large CUACs. Although DOE did not estimate consumer impacts for CUHPs, the results would be very similar to those for CUACs for the reasons stated in section V.B.1 of the direct final rule.

At TSL 5, the projected change in INPV ranges from a decrease of $ 881.9 million to an increase of $ 93.1 million, which corresponds to a change of -53.7 percent and 5.7 percent, respectively. The industry is expected to incur $ 591.0 million in total conversion costs at this level. DOE projects that 98.7 percent of current equipment listings would require redesign at this level to meet this standard level today. At this level, DOE recognizes that manufacturers could face technical resource constraints. Manufacturers stated they would require additional engineering expertise and additional test laboratory capacity. It is unclear whether manufacturers could complete the hiring of the necessary technical expertise and construction of the necessary test facilities in time to allow for the redesign of all equipment to meet max-tech by 2019. Furthermore, DOE recognizes that a standard set at max-tech could greatly limit equipment differentiation in the CUAC/CUHP market. By commoditizing a key differentiating feature, a standard set at max-tech would likely accelerate consolidaton in the industry.

The Secretary tentatively concludes that at TSL 5 for CUACs and CUHPs, the benefits of energy savings, positive NPV of consumer benefits, emission reductions, and the estimated monetary value of the emissions reductions would be outweighed by the economic burden on some consumers, and the impacts on manufacturers, including the conversion costs and profit margin impacts that could result in a large reduction in INPV. Consequently, the Secretary has tentatively concluded that TSL 5 is not economically justified.

DOE then considered TSL 4. TSL 4 would save 19.7 quads of energy, an amount DOE considers significant. Under TSL 4, the NPV of consumer benefit would be $ 19.2 billion using a discount rate of 7-percent, and $ 64.1 billion using a discount rate of 3-percent.

The cumulative emissions reductions at TSL 4 are 1,167 million Mt of CO[2], 610 thousand tons of SO[2], 2,180 thousand tons of NO[X], 2.25 tons of Hg, 5,215 thousand tons of CH[4,] and 12.80 thousand tons of N[2] O. The estimated monetary value of the CO[2] emissions reduction at TSL 4 ranges from $ 6.860 billion to $ 102.4 billion.

At TSL 4, the average LCC impact is a savings of $ 3,035 for small CUACs, $ 16,803 for large CUACs, and $ 18,386 for very large CUACs. The simple payback period is 2.5 years for small CUACs, 2.5 years for large CUACs, and 5.6 years for very large CUACs. The fraction of consumers experiencing a net LCC cost is 25 percent for small CUACs, 1 percent for large CUACs, and 3 percent for very large CUACs. Although DOE did not estimate consumer impacts for CUHPs, the results would be very similar to those for CUACs for the reasons stated in section V.B.1 of the direct final rule.

At TSL 4, the projected change in INPV ranges from a decrease of $ 619.6 million to an increase of $ 16.3 million, which corresponds to a change of -37.7 percent and 1.0 percent, respectively. The industry is expected to incur $ 538.8 million in total conversion costs at this level. DOE projects that 96.0 percent of current equipment listings would require redesign at this level to meet this standard level today.

The Secretary tentatively concludes that at TSL 4 for CUACs and CUHPs, the benefits of energy savings, positive NPV of consumer benefits, emission reductions, and the estimated monetary value of the emissions reductions would be outweighed by the economic burden on some consumers, and the impacts on manufacturers, including the conversion costs and profit margin impacts that could result in a reduction in INPV. Consequently, the Secretary has tentatively concluded that TSL 4 is not economically justified.

DOE then considered TSL 3.5. TSL 3.5 would save 16.4 quads of energy, an amount DOE considers significant. Under TSL 3.5, the NPV of consumer benefit would be $ 17.1 billion using a discount rate of 7-percent, and $ 55.3 billion using a discount rate of 3-percent.

The cumulative emissions reductions at TSL 3.5 are 973 million Mt of CO[2], 508 thousand tons of SO[2], 1,815 thousand tons of NO[X], 1.88 tons of Hg, 4,342 thousand tons of CH[4,] and 10.67 thousand tons of N[2] O. The estimated monetary value of the CO[2] emissions reduction at TSL 3.5 ranges from $ 5.729 billion to $ 85.44 billion.

At TSL 3.5, the average LCC impact is a savings of $ 3,517 for small CUACs, $ 12,266 for large CUACs, and $ 8,881 for very large CUACs. The simple payback period is 2.6 years for small CUACs, 2.6 years for large CUACs, and 7.2 years for very large CUACs. The fraction of consumers experiencing a net LCC cost is 13 percent for small CUACs, 1 percent for large CUAC, and 23 percent for very large CUACs. Although DOE did not estimate consumer impacts for CUHPs, the results would be very similar to those for CUACs for the reasons stated in section V.B.1 of the direct final rule.

At TSL 3.5, the projected change in INPV ranges from a decrease of $ 506.4 million to an increase of $ 25.7 million, which corresponds to a change of -30.8 percent and 1.6 percent, respectively. The industry is expected to incur $ 489.2 million in total conversion costs at this level. DOE projects that 93.5 percent of current equipment listings would **[\*2117]** require redesign at this level to meet this standard level today.

The Secretary tentatively concludes that at TSL 3.5 for CUACs and CUHPs, the benefits of energy savings, positive NPV of consumer benefits, emission reductions, and the estimated monetary value of the emissions reductions would be outweighed by the economic burden on some consumers, and the impacts on manufacturers, including the conversion costs and profit margin impacts that could result in a reduction in INPV. Consequently, the Secretary has tentatively concluded that TSL 3.5 is not economically justified.

DOE then considered TSL 3. TSL 3 would save 15.9 quads of energy, an amount DOE considers significant. Under TSL 3, the NPV of consumer benefit would be $ 16.8 billion using a discount rate of 7-percent, and $ 53.7 billion using a discount rate of 3-percent.

The cumulative emissions reductions at TSL 3 are 943 million Mt of CO[2], 493 thousand tons of SO[2], 1,759 thousand tons of NO[X], 1.82 tons of Hg, 4,208 thousand tons of CH[4], and 10.34 thousand tons of N[2] O. The estimated monetary value of the CO[2] emissions reduction at TSL 3 ranges from $ 5.556 billion to $ 82.83 billion.

At TSL 3, the average LCC impact is a savings of $ 4,233 for small CUACs, $ 10,135 for large CUACs, and $ 8,881 for very large CUACs. The simple payback period is 4.9 years for small CUACs, 2.6 years for large CUACs, and 7.2 years for very large CUACs. The fraction of consumers experiencing a net LCC cost is 5 percent for small CUACs, 2 percent for large CUAC, and 23 percent for very large CUACs. Although DOE did not estimate consumer impacts for CUHPs, the results would be very similar to those for CUACs for the reasons stated in section V.B.1 of the direct final rule.

At TSL 3, the projected change in INPV ranges from a decrease of $ 447.2 million to an increase of $ 52.4 million, which corresponds to a change of -27.2 percent and 3.2 percent, respectively. DOE projects that 81.6 percent of current equipment listings would require redesign at this level to meet this standard level today.

The Secretary tentatively concludes that at TSL 3 for CUACs and CUHPs, the benefits of energy savings, positive NPV of consumer benefits, emission reductions, and the estimated monetary value of the emissions reductions would be outweighed by the economic burden on some consumers, and the impacts on manufacturers, including the conversion costs and profit margin impacts that could result in a large reduction in INPV. Consequently, the Secretary has tentatively concluded that TSL 3 is not economically justified.

DOE then considered the Recommended TSL, which reflects the standard levels recommended by the Working Group. The Recommended TSL would save 14.8 quads of energy, an amount DOE considers significant. Under the Recommended TSL, the NPV of consumer benefit would be $ 15.2 billion using a discount rate of 7-percent, and $ 50.0 billion using a discount rate of 3-percent.

The cumulative emissions reductions at the Recommended TSL are 873 million Mt of CO[2], 454 thousand tons of SO[2], 1,634 thousand tons of NO[X], 1.68 tons of Hg, 3,917 thousand tons of CH[4], and 9.54 thousand tons of N[2] O. The estimated monetary value of the CO[2] emissions reduction at the Recommended TSL ranges from $ 5.046 billion to $ 75.94 billion.

At the Recommended TSL, the average LCC impact is a savings of $ 4,233 for small CUACs, $ 10,135 for large CUACs, and $ 8,610 for very large CUACs. The simple payback period is 4.9 years for small CUACs, 2.6 years for large CUACs, and 6.2 years for very large CUACs. The fraction of consumers experiencing a net LCC cost is 5 percent for small CUACs, 2 percent for large CUACs, and 7 percent for very large CUACs. Although DOE did not estimate consumer impacts for CUHPs, the results would be very similar to those for CUACs for the reasons stated in section V.B.1 of the direct final rule.

The Recommended TSL, as presented by the Working Group and approved by ASRAC, aligns the effective dates of the CUAC/CUHP and CWAF rulemakings. That approach adopts the ASHRAE 90.1-2013 efficiency levels in 2018 and a higher level in in 2023 as recommended by the Working Group. DOE anticipates that aligning the effective dates will reduce total conversion costs and cumulative regulatory burden, while also allowing industry to gain clarity on potential ***regulations*** that could affect refrigerant availability before the higher appliance standard takes effect in 2023. DOE projects that 31.5 percent of current equipment listings would require redesign at this level to meet the 2018 standard level, while 79.6 percent of current equipment listings would require redesign at this level to meet the 2023 standard level.

At the Recommended TSL, the projected change in INPV ranges from a decrease of $ 440.4 million to a decrease of $ 38.5 million, which corresponds to a change of -26.8 percent and -2.3 percent, respectively. The industry is expected to incur $ 520.8 million in total conversion costs at this level. However, the industry members of the Working Group noted that aligning the compliance dates for the CUAC/CUHP and CWAF standards in the manner recommended would allow manufacturers to coordinate their redesign and testing expenses for these equipment. (CUAC: AHRI and ACEEE, No. 80 at p. 1). With this coordination, manufacturers explained that there would be a reduction in the total conversion costs associated with the direct final rule. The resulting synergies from aligning the CUAC/CUHP and CWAF compliance dates would produce INPV impacts that are less severe than the forecasted INPV range of -26.8 percent to -2.3 percent.

After considering the analysis and weighing the benefits and burdens, DOE has tentatively determined that the recommended standards are in accordance with [*42 U.S.C. 6313(a)(6)(B)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=), which contains provisions for adopting a uniform national standard more stringent than the amended ASHRAE Standard 90.1 for the equipment considered in this document. Specifically, the Secretary has tentatively determined, supported by clear and convincing evidence that such adoption would result in the significant additional conservation of energy and is technologically feasible and economically justified. In determining whether the recommended standards are economically justified, the Secretary has tentatively determined that the benefits of the recommended standards exceed the burdens. Namely, the Secretary has tentatively concluded that under the recommended standards for CUACs and CUHPs, the benefits of energy savings, positive NPV of consumer benefits, emission reductions, the estimated monetary value of the emissions reductions, and positive average LCC savings would outweigh the negative impacts on some consumers and on manufacturers, including the conversion costs that could result in a reduction in INPV for manufacturers.

The proposed amended energy conservation standards for CUACs and CUHPs, which prescribe the minimum allowable IEER and, for commercial unitary heat pumps, COP, are shown in Table II.3. **[\*2118]**

| **Table II.3--Proposed Energy Conservation Standards for Small, Large, and Very** | | | | |
| --- | --- | --- | --- | --- |
| **Large Air-Cooled Commercial Package Air Conditioning and Heating Equipment** | | | | |
|  |  |  |  |  |
| **Equipment type** |  | **Heating type** | **Proposed** | **Compliance** |
|  |  |  | **energy** | **date** |
|  |  |  | **conservation** |  |
|  |  |  | **standard** |  |
| Small | AC | Electric | 12.9 IEER | January 1, |
| Commercial |  | Resistance | 14.8 IEER | 2018. |
| Packaged AC |  | Heating or No |  | January 1, |
| and HP |  | Heating |  | 2023. |
| (Air-Cooled)-- |  |  |  |  |
| >/= 65,000 |  |  |  |  |
| Btu/h and |  |  |  |  |
| <135,000 Btu/h |  |  |  |  |
| Cooling |  |  |  |  |
| Capacity |  |  |  |  |
|  |  | All Other | 12.7 IEER | January 1, |
|  |  | Types of | 14.6 IEER | 2018. |
|  |  | Heating |  | January 1, |
|  |  |  |  | 2023. |
|  | HP | Electric | 12.2 IEER | January 1, |
|  |  | Resistance | 3.3 COP | 2018. |
|  |  | Heating or No | 14.1 IEER |  |
|  |  | Heating | 3.4 COP | January 1, |
|  |  | All Other | 12.0 IEER | January 1, |
|  |  | Types of | 3.3 COP | 2018. |
|  |  | Heating | 13.9 IEER |  |
|  |  |  | 3.4 COP | January 1, |
| Large | AC | Electric | 12.4 IEER | January 1, |
| Commercial |  | Resistance | 14.2 IEER | 2018. |
| Packaged AC |  | Heating or No |  | January 1, |
| and HP |  | Heating |  | 2023. |
| (Air-Cooled)-- |  |  |  |  |
| >/= 135,000 |  |  |  |  |
| Btu/h and |  |  |  |  |
| <240,000 Btu/h |  |  |  |  |
| Cooling |  |  |  |  |
| Capacity |  |  |  |  |
|  |  | All Other | 12.2 IEER | January 1, |
|  |  | Types of | 14.0 IEER | 2018. |
|  |  | Heating |  | January 1, |
|  |  |  |  | 2023. |
|  | HP | Electric | 11.6 IEER | January 1, |
|  |  | Resistance | 3.2 COP | 2018. |
|  |  | Heating or No | 13.5 IEER |  |
|  |  | Heating | 3.3 COP | January 1, |
|  |  | All Other | 11.4 IEER | January 1, |
|  |  | Types of | 3.2 COP | 2018. |
|  |  | Heating | 13.3 IEER |  |
|  |  |  | 3.3 COP | January 1, |
| Very Large | AC | Electric | 11.6 IEER | January 1, |
| Commercial |  | Resistance | 13.2 IEER | 2018. |
| Packaged AC |  | Heating or No |  | January 1, |
| and HP |  | Heating |  | 2023. |
| (Air-Cooled)-- |  |  |  |  |
| >/= 240,000 |  |  |  |  |
| Btu/h and |  |  |  |  |
| <760,000 Btu/h |  |  |  |  |
| Cooling |  |  |  |  |
| Capacity |  |  |  |  |
|  |  | All Other | 11.4 IEER | January 1, |
|  |  | Types of | 13.0 IEER | 2018. |
|  |  | Heating |  | January 1, |
|  |  |  |  | 2023. |
|  | HP | Electric | 10.6 IEER | January 1, |
|  |  | Resistance | 3.2 COP | 2018. |
|  |  | Heating or No | 12.5 IEER |  |
|  |  | Heating | 3.2 COP | January 1, |
|  |  | All Other | 10.4 IEER | January 1, |
|  |  | Types of | 3.2 COP | 2018. |
|  |  | Heating | 12.3 IEER |  |
|  |  |  | 3.2 COP | January 1, |

**[\*2119]**

The benefits and costs of the proposed standards--which mimic those found in the direct final rule--can also be expressed in terms of annualized values. The annualized net benefit is the sum of: (1) The annualized national economic value (expressed in 2014] of the benefits from operating equipment that meet the adopted standards (consisting primarily of operating cost savings from using less energy, minus increases in product purchase costs, and (2) the annualized monetary value of the benefits of CO[2] and NO[X] emission reductions. n9

n9 To convert the time-series of costs and benefits into annualized values, DOE calculated a present value in 2014, the year used for discounting the NPV of total consumer costs and savings. For the benefits, DOE calculated a present value associated with each year's shipments in the year in which the shipments occur (2020, 2030, *etc.*), and then discounted the present value from each year to 2015. The calculation uses discount rates of 3- and 7-percent for all costs and benefits except for the value of CO[2] reductions, for which DOE used case-specific discount rates. Using the present value, DOE then calculated the fixed annual payment over a 30-year period, starting in the compliance year that yields the same present value.

Table II.4 shows the annualized values for CUACs and CUHPs under the Recommended TSL, expressed in 2014$ . The results under the primary estimate are as follows. Using a 7-percent discount rate for benefits and costs other than CO[2] reduction, (for which DOE used a 3-percent discount rate along with the SCC series that has a value of $ 40.0/t in 2015), n10 the estimated cost of the standards in this rule is $ 708 million per year in increased equipment costs, while the estimated annual benefits are $ 2,099 million in reduced equipment operating costs, $ 1,320 million in CO[2] reductions, and $ 147.5 million in reduced NO[X] emissions. In this case, the net benefit amounts to $ 2,859 million per year. Using a 3-percent discount rate for all benefits and costs and the SCC series has a value of $ 40.0/t in 2015, the estimated cost of the standards is $ 792 million per year in increased equipment costs, while the estimated annual benefits are $ 3,441 million in reduced operating costs, $ 1,320 million in CO[2] reductions, and $ 267.3 million in reduced NO[X] emissions. In this case, the net benefit amounts to $ 4,237 million per year.

n10 DOE used a 3-percent discount rate because the SCC values for the series used in the calculation were derived using a 3-percent discount rate.

| **Table II.4--Annualized Benefits and Costs of Proposed Standards for Small,** | | | | |
| --- | --- | --- | --- | --- |
| **Large, and Very Large Air-Cooled Commercial Package Air Conditioning and** | | | | |
| **Heating Equipment** | | | | |
|  |  |  |  |  |
|  |  | **Million 2014$/year** | | |
|  |  |  |  |  |
|  | **Discount rate** | **Primary** | **Low net** | **High net** |
|  | **(%)** | **estimate\*** | **benefits** | **benefits** |
|  |  |  | **estimate** | **estimate** |
| Benefits | | | | |
|  |  |  |  |  |
| Consumer | 7 | 2,099 | 2,021 | 2,309 |
| Operating Cost | 3 | 3,441 | 3,287 | 3,830 |
| Savings |  |  |  |  |
| CO[2] | 5 | 357 | 355 | 361 |
| Reduction |  |  |  |  |
| Value ( |  |  |  |  |
| $ 12.2/t |  |  |  |  |
| case)\*\* |  |  |  |  |
| CO[2] | 3 | 1,320 | 1,313 | 1,337 |
| Reduction |  |  |  |  |
| Value ( |  |  |  |  |
| $ 40.0/t |  |  |  |  |
| case)\*\* |  |  |  |  |
| CO[2] | 2.5 | 1,973 | 1,964 | 1,999 |
| Reduction |  |  |  |  |
| Value ( |  |  |  |  |
| $ 62.3/t |  |  |  |  |
| case)\*\* |  |  |  |  |
| CO[2] | 3 | 4,028 | 4,009 | 4,080 |
| Reduction |  |  |  |  |
| Value ( |  |  |  |  |
| $ 117/t |  |  |  |  |
| case)\*\* |  |  |  |  |
| NO[X] | 7 | 147.5 | 146.7 | 149.5 |
| Reduction | 3 | 267.3 | 265.9 | 270.7 |
| Value+ |  |  |  |  |
| Total | 7% plus | 2,603 to | 2,522 to | 2,820 to |
| Benefits+ + | CO[2] range | 6,275 | 6,176 | 6,539 |
|  | 7 | 3,566 | 3,481 | 3,796 |
|  | 3 plus | 4,065 to | 3,908 to | 4,462 to |
|  | CO[2] range | 7,737 | 7,561 | 8,181 |
|  | 3 | 5,028 | 4,866 | 5,438 |
| Costs | | | | |
|  |  |  |  |  |
| Consumer | 7 | 708 | 888 | 275 |
| Incremental | 3 | 792 | 1028 | 231 |
| Product Costs |  |  |  |  |
| Net Benefits | | | | |
|  |  |  |  |  |
| Total+ + | 7% plus | 1,895 to | 1,635 to | 2,546 to |
|  | CO[2] range | 5,567 | 5,288 | 6,265 |
|  | 7 | 2,859 | 2,593 | 3,521 |
|  | 3 plus | 3,274 to | 2,879 to | 4,232 to |
|  | CO[2] range | 6,945 | 6,533 | 7,951 |
|  | 3 | 4,237 | 3,838 | 5,207 |

\* This table presents the annualized costs and benefits associated with CUACs and CUHPs shipped in 2018-2048. These results include benefits to consumers which accrue after 2048 from the CUACs and CUHPs purchased in 2018-2048. The results account for the incremental variable and fixed costs incurred by manufacturers due to the standard, some of which may be incurred in preparation for the rule. The Primary, Low Benefits, and High Benefits estimates utilize projections of energy prices from the AEO 2015 Reference case, Low Economic Growth case, and High Economic Growth case, respectively. In addition, incremental product costs reflect a constant price trend in the Primary estimate, a slightly increasing price trend in the Low Benefits estimate, and a slightly decreasing price trend in the Low Benefits estimate. The methods used to project price trends are explained in section IV.D.1.

\*\* The CO[2] values represent global monetized values of the SCC, in 2014$, in 2015 under several scenarios of the updated SCC values. The first three cases use the averages of SCC distributions calculated using 5%, 3%, and 2.5% discount rates, respectively. The fourth case represents the 95th percentile of the SCC distribution calculated using a 3% discount rate. The SCC time series incorporate an escalation factor. + Total Benefits for both the 3% and 7% cases are derived using the series corresponding to the average SCC with 3-percent discount rate ($ 40.0/t) case. In the rows labeled "7% plus CO[2] range" and "3% plus CO[2] range," the operating cost and NO[X] benefits are calculated using the labeled discount rate, and those values are added to the full range of CO[2] values.

+ The $/ton values used for NO[X] are described in section IV.L.2 of the direct final rule. DOE estimated the monetized value of NOx emissions reductions using benefit per ton estimates from the Regulatory Impact Analysis titled, "Proposed Carbon Pollution Guidelines for Existing Power Plants and Emission Standards for Modified and Reconstructed Power Plants," published in June 2014 by EPA's Office of Air Quality Planning and Standards. (Available at: [*http://www3.epa.gov/ttnecas1/regdata/RIAs/111dproposalRIAfinal0602.pdf*](http://www3.epa.gov/ttnecas1/regdata/RIAs/111dproposalRIAfinal0602.pdf).) For DOE's Primary Estimate and Low Net Benefits Estimate, the agency is presenting a national benefit-per-ton estimate for particulate matter emitted from the Electric Generating Unit sector based on an estimate of premature mortality derived from the ACS study (Krewski et al., 2009). For DOE's High Net Benefits Estimate, the benefit-per-ton estimates were based on the Six Cities study (Lepuele et al., 2011), which are nearly two-and-a-half times larger than those from the ACS study. Because of the sensitivity of the benefit-per-ton estimate to the geographical considerations of sources and receptors of emission, DOE intends to investigate refinements to the agency's current approach of one national estimate by assessing the regional approach taken by EPA's Regulatory Impact Analysis for the Clean Power Plan Final Rule.

+ + Total Benefits for both the 3% and 7% cases are derived using the series corresponding to the average SCC with 3-percent discount rate ($ 40.0/t) case. In the rows labeled "7% plus CO[2] range" and "3% plus CO[2] range," the operating cost and NO[X] benefits are calculated using the labeled discount rate, and those values are added to the full range of CO[2] values.

*B. Benefits and Burdens of TSLs Considered for Commercial Warm Air Furnaces*

Table II.5 and Table II.6 summarize the quantitative impacts estimated for each TSL for CWAFs. For TSL 2, the national impacts are projected over the lifetime of equipment sold in 2023-2048. For the other TSLs, the impacts are projected over the lifetime of equipment sold in 2019-2048. The energy savings, emissions reductions, and value of emissions reductions refer to full-fuel-cycle results. The efficiency levels contained in each TSL are described in section V.A of the direct final rule.

| **Table II.5--Summary of Analytical Results for Commercial Warm Air Furnaces:** | | | | | |
| --- | --- | --- | --- | --- | --- |
| **National Impacts** | | | | | |
|  |  |  |  |  |  |
|  | **Trial standard level** | | | | |
|  |  |  |  |  |  |
|  | **1** | **2** | **3** | **4** | **5** |
| Cumulative | 0.25 | 0.23 | 0.41 | 0.41 | 2.4 |
| FFC Energy |  |  |  |  |  |
| Savings |  |  |  |  |  |
| Quads |  |  |  |  |  |
| NPV of consumer costs and benefits 2014$ billion | | | | | |
|  |  |  |  |  |  |
| 3% discount | 1.1 | 1.0 | -0.1 | -0.1 | 2.6 |
| rate |  |  |  |  |  |
| 7% discount | 0.4 | 0.3 | -0.4 | -0.4 | -0.4 |
| rate |  |  |  |  |  |
| Cumulative FFC emissions reduction | | | | | |
|  |  |  |  |  |  |
| CO[2] | 13.4 | 12.4 | 22.0 | 22.0 | 126 |
| million |  |  |  |  |  |
| metric tons |  |  |  |  |  |
| SO[2] | 0.40 | 0.40 | 0.63 | 0.67 | -10.2 |
| thousand |  |  |  |  |  |
| tons |  |  |  |  |  |
| NO[X] | 43.0 | 41.2 | 70.5 | 72.2 | 473 |
| thousand |  |  |  |  |  |
| tons |  |  |  |  |  |
| Hg tons | 0.001 | 0.001 | 0.002 | 0.002 | -0.04 |
| CH[4] | 159 | 146 | 260 | 260 | 1,673 |
| thousand |  |  |  |  |  |
| tons |  |  |  |  |  |
| CH[4] | 4,440 | 4,096 | 7,289 | 7,292 | 46,831 |
| thousand |  |  |  |  |  |
| tons CO2eq\* |  |  |  |  |  |
| N[2]O | 0.03 | 0.03 | 0.05 | 0.06 | 0.08 |
| thousand |  |  |  |  |  |
| tons |  |  |  |  |  |
| N[2]O | 8.8 | 8.4 | 14.3 | 14.6 | 21.2 |
| thousand |  |  |  |  |  |
| tons CO2eq\* |  |  |  |  |  |
| Value of emissions reduction | | | | | |
|  |  |  |  |  |  |
| CO[2] | 79.8 to | 71.4 to | 126 to | 126 to | 713 to |
| 2014$ | 1,185 | 1,078 | 1,891 | 1,897 | 10,809 |
| million\*\* |  |  |  |  |  |
| NO[X]--3% | 120 to 264 | 110 to 243 | 188 to 414 | 192 to 424 | 1258 to |
| discount |  |  |  |  | 2772 |
| rate 2014$ |  |  |  |  |  |
| million |  |  |  |  |  |
| NO[X]--7% | 42.3 to | 36.1 to | 64.2 to 144 | 65.9 to 147 | 423 to 945 |
| discount | 94.4 | 80.9 |  |  |  |
| rate 2014$ |  |  |  |  |  |
| million |  |  |  |  |  |

For TSL 2, the impacts are projected over the lifetime of equipment sold in 2023-2048. For the other TSLs, the impacts are projected over the lifetime of equipment sold in 2019-2048.

\* CO[2]eq is the quantity of CO[2] that would have the same global warming potential (GWP).

\*\* Range of the economic value of CO[2] reductions is based on estimates of the global benefit of reduced CO[2] emissions.

| **Table II.6--Summary of Analytical Results for Commercial Warm Air Furnaces:** | | | | | |
| --- | --- | --- | --- | --- | --- |
| **Manufacturer and Consumer Impacts\*** | | | | | |
|  |  |  |  |  |  |
|  | **Trial standard level** | | | | |
|  |  |  |  |  |  |
| **Category** | **1** | **2** | **3** | **4** | **5** |
| Manufacturer Impacts | | | | | |
|  |  |  |  |  |  |
| Industry NPV | 85.8 to | 83.0 to | 65.5 to | 60.4 to | (19.3) to |
| (2014$ million) | 92.6 | 90.5 | 125.2 | 124.8 | 143.5 |
| (No-New-Standards |  |  |  |  |  |
| Case INPV = 96.3) |  |  |  |  |  |
| Industry NPV (% | (11.0) to | (13.9) to | (32.0) to | (37.3) to | (120.1) to |
| change) | (3.9) | (6.1) | 29.9 | 29.5 | 49.0 |
| Consumer average LCC savings (2014] | | | | | |
|  |  |  |  |  |  |
| Gas-Fired | $ 284 | $ 284 | $ 75 | $ 75 | $ 766 |
| Commercial Warm |  |  |  |  |  |
| Air Furnaces |  |  |  |  |  |
| Oil-Fired | NA | $ 400 | NA | $ 400 | $ 1,817 |
| Commercial Warm |  |  |  |  |  |
| Air Furnaces |  |  |  |  |  |
| Average\* | $ 284 | $ 285 | $ 75 | $ 79 | $ 781 |
| Consumer simple PBP (years) | | | | | |
|  |  |  |  |  |  |
| Gas-Fired | 1.4 | 1.4 | 12.3 | 12.3 | 11.3 |
| Commercial Warm |  |  |  |  |  |
| Air Furnaces |  |  |  |  |  |
| Oil-Fired | NA | 1.9 | NA | 1.9 | 7.5 |
| Commercial Warm |  |  |  |  |  |
| Air Furnaces |  |  |  |  |  |
| Average\* | 1.4 | 1.4 | 12.3 | 12.1 | 11.3 |
| % of Consumers that Experience Net Cost | | | | | |
|  |  |  |  |  |  |
| Gas-Fired | 6% | 6% | 58% | 58% | 58% |
| Commercial Warm |  |  |  |  |  |
| Air Furnaces |  |  |  |  |  |
| Oil-Fired | 0% | 11% | 0% | 11% | 54% |
| Commercial Warm |  |  |  |  |  |
| Air Furnaces |  |  |  |  |  |

\* Weighted by shares of each equipment class in total projected shipments in 2019.

+ At max tech, the standard will likely require CWAF manufacturers to make design changes to the cooling components of commercial HVAC products and to the chassis that houses the heating and cooling components. Because these cooling system changes are triggered by the CWAF standard, they are taken into account in the MIA's estimate of conversion costs. The additional expense of updating the commercial cooling product contributes to an INPV loss that is greater than 100%.

DOE first considered TSL 5, which represents the max-tech efficiency levels. TSL 5 would save 2.4 quads of energy, an amount DOE considers significant. Under TSL 5, the NPV of consumer cost would be $ 0.4 billion using a 7-percent discount rate, and the NPV of consumer benefit would be $ 2.6 billion using a 3-percent discount rate.

The cumulative emissions reductions at TSL 5 are 126 Mt of CO[2], 473 thousand tons of NO[X], 1,673 thousand tons of CH[4,] and 0.08 thousand tons of N[2] O. Projected emissions show an increase of 10.2 thousand tons of SO[2] and 0.04 ton of Hg. The estimated monetary value of the CO[2] emissions reduction at TSL 5 ranges from $ 713 million to $ 10,809 million.

At TSL 5, the average LCC impact is a savings of $ 766 for gas-fired CWAFs and $ 1,817 for oil-fired CWAFs. The simple payback period is 11.3 years for gas-fired CWAFs and 7.5 years for oil-fired CWAFs. The fraction of consumers experiencing a net LCC cost is 58 percent for gas-fired CWAF and 54 percent for oil-fired CWAFs.

At TSL 5, the projected change in INPV ranges from a decrease of $ 115.7 million to an increase of $ 47.2 million, which corresponds to a change of -120.1 percent and 49.0 percent, respectively. The industry is expected to incur $ 157.5 million in total conversion costs at this level. DOE projects that 99 percent of current equipment listings would require redesign at this level.

The Secretary tentatively concludes that at TSL 5 for CWAFs, the benefits of energy savings, positive NPV of consumer benefits using a discount rate of 3 percent, emission reductions, and the estimated monetary value of the emissions reductions would be outweighed by the economic burden on most consumers, the negative NPV of consumer benefits using a 7-percent discount rate, and the impacts on manufacturers, including the conversion costs and profit margin impacts that could result in a large reduction in INPV. Consequently, the Secretary has tentatively concluded that TSL 5 is not economically justified.

DOE then considered TSL 4. TSL 4 would save 0.41 quads of energy, an amount DOE considers significant. Under TSL 4, the NPV of consumer cost would be $ 0.4 billion using a 7-percent discount rate, and $ 0.1 billion using a 3-percent discount rate.

The cumulative emissions reductions at TSL 4 are 22 Mt of CO[2], 0.67 thousand tons of SO[2], 72.2 thousand tons of NO[X], 0.002 ton of Hg, 260 thousand tons of CH[4,] and 0.06 thousand tons of N[2] O. The estimated monetary value of the CO[2] emissions reduction at TSL 4 ranges from $ 126 million to $ 1,897 million.

At TSL 4, the average LCC impact is a savings of $ 75 for gas-fired CWAFs and $ 400 for oil-fired CWAFs. The simple payback period is 12.3 years for gas-fired CWAFs and 1.9 years for oil-fired CWAFs. The fraction of consumers experiencing a net LCC cost is 58 percent for gas-fired CWAFs, and 11 percent for oil-fired CWAFs.

At TSL 4, the projected change in INPV ranges from a decrease of $ 35.9 million to an increase of $ 28.4 million, which corresponds to a change of -37.3 percent and 29.5 percent, respectively. The industry is expected to incur $ 47.6 million in total conversion costs at this level. DOE projects that 94 percent of current product listings would require redesign at this level.

The Secretary tentatively concludes that at TSL 4 for CWAFs, the benefits of energy savings, emission reductions, and the estimated monetary value of the emissions reductions would be outweighed by the economic burden on many consumers, negative NPV of consumer benefits, and the impacts on manufacturers, including the conversion costs and profit margin impacts that could result in a large reduction in INPV. Consequently, the Secretary has tentatively concluded that TSL 4 is not economically justified.

DOE then considered TSL 3. TSL 3 would save 0.41 quads of energy, an amount DOE considers significant. Under TSL 3, the NPV of consumer cost would be $ 0.4 billion using a 7-percent discount rate, and $ 0.1 billion using a 3-percent discount rate.

The cumulative emissions reductions at TSL 3 are 22 Mt of CO[2], 0.63 thousand tons of SO[2], 70.5 thousand tons of NO[X], 0.002 ton of Hg, 260 thousand tons of CH[4,] and 0.05 thousand tons of N[2] O. The estimated monetary value of the CO[2] emissions reduction at TSL 3 ranges from $ 126 million to $ 1,891 million.

At TSL 3, the average LCC impact is a savings of $ 75 for gas-fired CWAFs. The simple payback period is 12.3 years for gas-fired CWAFs. The fraction of consumers experiencing a net LCC cost is 58 percent for gas-fired CWAFs. The EL at TSL 3 for oil-fired CWAFs is the baseline, so there are no LCC impacts for oil-fired CWAFs at TSL 3.

At TSL 3, the projected change in INPV ranges from a decrease of $ 30.9 million to an increase of $ 28.8 million, which corresponds to a change of -32.0 percent and 29.9 percent, respectively. The industry is expected to incur $ 41.0 million in total conversion costs at this level. DOE projects that 91 percent of current equipment listings would require redesign at this level.

The Secretary tentatively concludes that at TSL 3 for CWAFs, the benefits of **[\*2122]** energy savings, emission reductions, and the estimated monetary value of the emissions reductions would be outweighed by the economic burden on many consumers, negative NPV of consumer benefits, and the impacts on manufacturers, including the conversion costs and profit margin impacts that could result in a large reduction in INPV. Consequently, the Secretary has tentatively concluded that TSL 3 is not economically justified.

DOE then considered TSL 2, which corresponds to the recommendations by the Working Group. TSL 2 would save 0.23 quads of energy, an amount DOE considers significant. Under TSL 2, the NPV of consumer benefit would be $ 0.3 billion using a 7-percent discount rate, and $ 1.0 billion using a 3-percent discount rate.

The cumulative emissions reductions at TSL 2 are 12.4 Mt of CO[2], 0.40 thousand tons of SO[2], 41.2 thousand tons of NO[X], 0.001 ton of Hg, 146 thousand tons of CH[4,] and 0.03 thousand tons of N[2] O. The estimated monetary value of the CO[2] emissions reduction at TSL 2 ranges from $ 71.4 million to $ 1,078 million.

At TSL 2, the average LCC impact is a savings of $ 284 for gas-fired CWAFs and $ 400 for oil-fired CWAFs. The simple payback period is 1.4 years for gas-fired CWAF and 1.9 years for oil-fired CWAFs. The fraction of consumers experiencing a net LCC cost is 6 percent for gas-fired CWAFs and 11 percent for oil-fired CWAFs.

At TSL 2, 57 percent of current equipment listings would require redesign at this level. The projected change in INPV ranges from a decrease of $ 13.4 million to a decrease of $ 5.9 million, which corresponds to a decrease of 13.9 percent and 6.1 percent, respectively. The CWAF industry is expected to incur $ 22.2 million in total conversion costs. However, the industry noted that aligning the compliance dates for the CUAC/CUHP and CWAF standards, as recommended by the Working Group, would allow manufacturers to coordinate their redesign and testing expenses for this equipment. If this occurs, there could be a reduction in the total conversion costs associated with the DFR. The resulting synergies from aligning the compliance dates of the CUAC/CUHP and CWAF standards would produce INPV impacts that are less severe than the forecasted INPV range of -13.9 percent to -6.1 percent.

After considering the analysis and weighing the benefits and burdens, DOE has tentatively determined that the recommended standards are in accordance with [*42 U.S.C. 6313(a)(6)(B)*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GSK1-NRF4-43W1-00000-00&context=), which contains provisions for adopting a uniform national standard more stringent than the amended ASHRAE/IES Standard 90.1 for the equipment considered in this document. Specifically, the Secretary has tentatively determined, supported by clear and convincing evidence, that such adoption would result in significant additional conservation of energy and is technologically feasible and economically justified. In determining whether the recommended standards are economically justified, the Secretary has tentatively determined that the benefits of the recommended standards exceed the burdens. Namely, the Secretary has tentatively concluded that under the recommended standards for CWAFs, the benefits of energy savings, positive NPV of consumer benefits, emission reductions, the estimated monetary value of the emissions reductions, and positive average LCC savings would outweigh the negative impacts on some consumers and on manufacturers, including the conversion costs that could result in a reduction in INPV for manufacturers.

Based on the above analyses, DOE is proposing to amend the energy conservation standards for CWAFs--as expressed in terms of thermal efficiency--in the manner shown in Table II.7.

| **Table II.7--Proposed Energy Conservation Standards for Commercial Warm Air** | | |
| --- | --- | --- |
| **Furnaces** | | |
|  |  |  |
| **Equipment type** | **Input capacity (Btu/h)** | **Thermal** |
|  |  | **efficiency** |
|  |  | **(%)** |
| Gas-fired CWAFs | >/= 225,000 | 81 |
|  | Btu/h |  |
| Oil-fired CWAFs | >/= 225,000 | 82 |
|  | Btu/h |  |

The benefits and costs of the proposed standards can also be expressed in terms of annualized values. The annualized net benefit is the sum of: (1) The annualized national economic value (expressed in 2014] of the benefits from operating equipment that meet the adopted standards (consisting primarily of operating cost savings from using less energy, minus increases in equipment purchase costs), and (2) the annualized monetary value of the benefits of CO[2] and NO[X] emission reductions.

Table II.8 shows the annualized values for CWAFs under TSL 2, expressed in 2014$ . The results under the primary estimate are as follows. Using a 7-percent discount rate for benefits and costs other than CO[2] reductions, (for which DOE used a 3-percent discount rate along with the average SCC series corresponding to a value of $ 40.0/ton in 2015 (2014]), the estimated cost of the adopted standards for CWAFs is $ 4.31 million per year in increased equipment costs, while the estimated benefits are $ 49.0 million per year in reduced equipment operating costs, $ 24 million per year in CO[2] reductions, and $ 5.49 million per year in reduced NO[X] emissions. In this case, the net benefit amounts to $ 75 million per year.

Using a 3-percent discount rate for all benefits and costs and the average SCC series corresponding to a value of $ 40.0/ton in 2015 (in 2014], the estimated cost of the adopted standards for CWAFs is $ 4.38 million per year in increased equipment costs, while the estimated benefits are $ 71 million per year in reduced operating costs, $ 24.3 million per year in CO[2] reductions, and $ 8.76 million per year in reduced NO[X] emissions. In this case, the net benefit amounts to $ 100 million per year. **[\*2123]**

| **Table II.8--Annualized Benefits and Costs of Proposed Standards (TSL 2) for** | | | | |
| --- | --- | --- | --- | --- |
| **Commercial Warm Air Furnaces** | | | | |
|  |  |  |  |  |
|  | **Million 2014$/year** | | | |
|  |  |  |  |  |
|  | **Discount** | **Primary** | **Low** | **High** |
|  | **rate** | **estimate \*** | **net benefits** | **net benefits** |
|  | **%** |  | **estimate \*** | **estimate \*** |
| Benefits | | | | |
|  |  |  |  |  |
| Consumer | 7 | 49 | 48 | 54 |
| Operating Cost | 3 | 71 | 70 | 81 |
| Savings |  |  |  |  |
| CO[2] | 5 | 6.99 | 7.08 | 7.37 |
| Reduction |  |  |  |  |
| Value ( |  |  |  |  |
| $ 12.2/t |  |  |  |  |
| case)\*\* |  |  |  |  |
| CO[2] | 3 | 24 | 25 | 26 |
| Reduction |  |  |  |  |
| Value ( |  |  |  |  |
| $ 40.0/t |  |  |  |  |
| case)\*\* |  |  |  |  |
| CO[2] | 2.5 | 36 | 36 | 38 |
| Reduction |  |  |  |  |
| Value ( |  |  |  |  |
| $ 62.3/t |  |  |  |  |
| case)\*\* |  |  |  |  |
| CO[2] | 3 | 74 | 75 | 79 |
| Reduction |  |  |  |  |
| Value ( |  |  |  |  |
| $ 117/t |  |  |  |  |
| case)\*\* |  |  |  |  |
| NO[X] | 7 | 5 to 11 | 5 to 11 | 5 to 11 |
| Reduction | 3 | 8 to 17 | 8 to 17 | 8 to 18 |
| Value+ |  |  |  |  |
| Total | 7 plus CO[2] | 61 to 134 | 60 to 134 | 67 to 144 |
| Benefits+ + | range |  |  |  |
|  | 7 | 78 | 78 | 85 |
|  | 3 plus CO[2] | 86 to 162 | 84 to 162 | 96 to 177 |
|  | range |  |  |  |
|  | 3 | 103 | 102 | 114 |
| Costs | | | | |
|  |  |  |  |  |
| Consumer | 7 | 4.31 | 5.04 | 3.92 |
| Incremental | 3 | 4.38 | 5.22 | 3.94 |
| Installed |  |  |  |  |
| Costs |  |  |  |  |
| Net Benefits | | | | |
|  |  |  |  |  |
| Total+ + | 7 plus CO[2] | 57 to 130 | 55 to 129 | 63 to 140 |
|  | range |  |  |  |
|  | 7 | 74 | 72 | 81 |
|  | 3 plus CO[2] | 82 to 158 | 79 to 157 | 92 to 173 |
|  | range |  |  |  |
|  | 3 | 99 | 97 | 110 |

\*This table presents the annualized costs and benefits associated with CWAFs shipped in 2023-2048. These results include benefits to consumers which accrue after 2048 from the CWAFs purchased from 2023-2048. The results account for the incremental variable and fixed costs incurred by manufacturers due to the standard, some of which may be incurred in preparation for the rule. The Primary, Low Benefits, and High Benefits Estimates utilize projections of energy prices from the AEO 2015 Reference case, Low Economic Growth case, and High Economic Growth case, respectively. In addition, incremental equipment costs reflect a medium decline rate in the Primary Estimate, a low decline rate in the Low Benefits Estimate, and a high decline rate in the High Benefits Estimate.

\*\*The CO[2] values represent global monetized values of the SCC, in 2014$, in 2015 under several scenarios of the updated SCC values. The first three cases use the averages of SCC distributions calculated using 5%, 3%, and 2.5% discount rates, respectively. The fourth case represents the 95th percentile of the SCC distribution calculated using a 3% discount rate. The SCC time series incorporate an escalation factor.

+ The $/ton values used for NO[X] are described in the Direct Final Rule. DOE estimated the monetized value of NOx emissions reductions using benefit per ton estimates from the Regulatory Impact Analysis titled, "Proposed Carbon Pollution Guidelines for Existing Power Plants and Emission Standards for Modified and Reconstructed Power Plants," published in June 2014 by EPA's Office of Air Quality Planning and Standards. (Available at: [*http://www3.epa.gov/ttnecas1/regdata/RIAs/111dproposalRIAfinal0602.pdf*](http://www3.epa.gov/ttnecas1/regdata/RIAs/111dproposalRIAfinal0602.pdf).) For DOE's Primary Estimate and Low Net Benefits Estimate, the agency is presenting a national benefit-per-ton estimate for particulate matter emitted from the Electric Generating Unit sector based on an estimate of premature mortality derived from the ACS study (Krewski et al., 2009). For DOE's High Net Benefits Estimate, the benefit-per-ton estimates were based on the Six Cities study (Lepuele et al., 2011), which are nearly two-and-a-half times larger than those from the ACS study. Because of the sensitivity of the benefit-per-ton estimate to the geographical considerations of sources and receptors of emission, DOE intends to investigate refinements to the agency's current approach of one national estimate by assessing the regional approach taken by EPA's Regulatory Impact Analysis for the Clean Power Plan Final Rule.

+ + Total Benefits for both the 3% and 7% cases are derived using the series corresponding to the average SCC with 3-percent discount rate ($ 40.0/t case. In the rows labeled "7% plus CO[2] range" and "3% plus CO[2] range," the operating cost and NO[X] benefits are calculated using the labeled discount rate, and those values are added to the full range of CO[2] values.

**III. Public Participation**

*Submission of Comments*

DOE will accept comments, data, and information regarding this proposed rule before or after the public meeting, but no later than the date provided in the **DATES** section at the beginning of this proposed rule. Interested parties may submit comments, data, and other information using any of the methods described in the **ADDRESSES** section at the beginning of this document.

Submitting comments via [*www.****regulations****.gov*](http://www.regulations.gov)*.* The [*www.****regulations****.gov*](http://www.regulations.gov) Web page will require you to provide your name and contact information. Your contact information will be viewable to DOE Building Technologies staff only. Your contact information will not be publicly viewable except for your first and last names, organization name (if any), and submitter representative name (if any). If your comment is not processed properly because of technical difficulties, DOE will use this information to contact you. If DOE cannot read your comment due to technical difficulties and cannot contact you for clarification, DOE may not be able to consider your comment.

However, your contact information will be publicly viewable if you include it in the comment itself or in any documents attached to your comment. Any information that you do not want to be publicly viewable should not be included in your comment, nor in any document attached to your comment. Otherwise, persons viewing comments will see only first and last names, organization names, correspondence containing comments, and any documents submitted with the comments.

Do not submit to [*www.****regulations****.gov*](http://www.regulations.gov) information for which disclosure is restricted by statute, such as trade secrets and commercial or financial information (hereinafter referred to as **[\*2124]** Confidential Business Information ("CBI")). Comments submitted through [*www.****regulations****.gov*](http://www.regulations.gov) cannot be claimed as CBI. Comments received through the Web site will waive any CBI claims for the information submitted. For information on submitting CBI, see the Confidential Business Information section below.

DOE processes submissions made through [*www.****regulations****.gov*](http://www.regulations.gov) before posting. Normally, comments will be posted within a few days of being submitted. However, if large volumes of comments are being processed simultaneously, your comment may not be viewable for up to several weeks. Please keep the comment tracking number that [*www.****regulations****.gov*](http://www.regulations.gov) provides after you have successfully uploaded your comment.

*Submitting comments via email, hand delivery/courier, or mail.* Comments and documents submitted via email, hand delivery/courier, or mail also will be posted to [*www.****regulations****.gov*](http://www.regulations.gov)*.* If you do not want your personal contact information to be publicly viewable, do not include it in your comment or any accompanying documents. Instead, provide your contact information in a cover letter. Include your first and last names, email address, telephone number, and optional mailing address. The cover letter will not be publicly viewable as long as it does not include any comments

Include contact information each time you submit comments, data, documents, and other information to DOE. If you submit via mail or hand delivery/courier, please provide all items on a CD, if feasible, in which case it is not necessary to submit printed copies. No telefacsimiles (faxes) will be accepted.

Comments, data, and other information submitted to DOE electronically should be provided in PDF (preferred), Microsoft Word or Excel, WordPerfect, or text (ASCII) file format. Provide documents that are not secured, that are written in English, and that are free of any defects or viruses. Documents should not contain special characters or any form of encryption and, if possible, they should carry the electronic signature of the author.

*Campaign form letters.* Please submit campaign form letters by the originating organization in batches of between 50 to 500 form letters per PDF or as one form letter with a list of supporters' names compiled into one or more PDFs. This reduces comment processing and posting time.

*Confidential Business Information.* Pursuant to [*10 CFR 1004.11*](https://advance.lexis.com/api/document?collection=administrative-codes&id=urn:contentItem:5PWY-CVX0-008G-Y2NC-00000-00&context=), any person submitting information that he or she believes to be confidential and exempt by law from public disclosure should submit via email, postal mail, or hand delivery/courier two well-marked copies: one copy of the document marked "confidential" including all the information believed to be confidential, and one copy of the document marked "non-confidential" with the information believed to be confidential deleted. Submit these documents via email or on a CD, if feasible. DOE will make its own determination about the confidential status of the information and treat it according to its determination.

Factors of interest to DOE when evaluating requests to treat submitted information as confidential include: (1) A description of the items; (2) whether and why such items are customarily treated as confidential within the industry; (3) whether the information is generally known by or available from other sources; (4) whether the information has previously been made available to others without obligation concerning its confidentiality; (5) an explanation of the ***competitive*** injury to the submitting person that would result from public disclosure; (6) when such information might lose its confidential character due to the passage of time; and (7) why disclosure of the information would be contrary to the public interest.

It is DOE's policy that all comments may be included in the public docket, without change and as received, including any personal information provided in the comments (except information deemed to be exempt from public disclosure).

**IV. Procedural Issues and Regulatory Review**

The regulatory reviews conducted for this proposed rule are identical to those conducted for the direct final rule published elsewhere in this **Federal Register** . Please see the direct final rule for further details.

**V. Approval of the Office of the Secretary**

The Secretary of Energy has approved publication of this proposed rule.

***Regulations***

**List of Subjects in 10 CFR Part 431**

Administrative practice and procedure, Confidential business information, Energy conservation, Household appliances, Imports, Intergovernmental relations, Reporting and recordkeeping requirements, Small businesses.

Issued in Washington, DC, on December 17, 2015.

**David T. Danielson,**

*Assistant Secretary, Energy Efficiency and Renewable Energy.*

For the reasons set forth in the preamble, DOE proposes to amend part 431 of chapter II, subchapter D, of title 10 of the Code of Federal ***Regulations***, to read as set forth below:

1. **ROGRAM FOR CERTAIN COMMERCIAL AND INDUSTRIAL EQUIPMENT**
2. The authority citation for part 431 continues to read as follows:

**Authority:** [*42 U.S.C. 6291*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GN51-NRF4-412F-00000-00&context=)-[*6317*](https://advance.lexis.com/api/document?collection=statutes-legislation&id=urn:contentItem:4YF7-GRW1-NRF4-420B-00000-00&context=).

1. Section 431.77 is revised to read as follows:
2. **tandards and their effective dates.**
3. ***air furnaces.***Each gas-fired commercial warm air furnace must meet the following energy efficiency standard levels:
4. For gas-fired commercial warm air furnaces manufactured starting on January 1, 1994, until January 1, 2023, the TE at the maximum rated capacity (rated maximum input) must be not less than 80 percent; and
5. For gas-fired commercial warm air furnaces manufactured starting on January 1, 2023, the TE at the maximum rated capacity (rated maximum input) must be not less than 81 percent.
6. ***air furnaces.***Each oil-fired commercial warm air furnace must meet the following energy efficiency standard levels:
7. For oil-fired commercial warm air furnaces manufactured starting on January 1, 1994, until January 1, 2023, the TE at the maximum rated capacity (rated maximum input) must be not less than 81 percent; and
8. For oil-fired commercial warm air furnaces manufactured starting on January 1, 2023, the TE at the maximum rated capacity (rated maximum input) must be not less than 82 percent.
9. Section 431.92 is amended by adding the definition of "Double-duct air conditioner or heat pump means air-cooled commercial package air conditioning and heating equipment" in alphabetical order to read as follows:
10. **g commercial air conditioners and heat pumps.**

\*    \*    \*    \*    \*

*Double-duct air conditioner or heat pump means air-cooled commercial* ***[\*2125]*** *package air conditioning and heating equipment* that--

1. Is either a horizontal single package or split-system unit; or a vertical unit that consists of two components that may be shipped or installed either connected or split;
2. Is intended for indoor installation with ducting of outdoor air from the building exterior to and from the unit, as evidenced by the unit and/or all of its components being non-weatherized, including the absence of any marking (or listing) indicating compliance with UL 1995, "Heating and Cooling Equipment," or any other equivalent requirements for outdoor use;
3. If it is a horizontal unit, a complete unit has a maximum height of 35 inches;
4. If it is a vertical unit, a complete unit has a maximum depth of 35 inches; and
5. Has a rated cooling capacity greater than or equal to 65,000 Btu/h and up to 300,000 Btu/h.

   \*    \*    \*    \*    \*

1. Section 431.97 is amended by:
2. Redesignating Tables 5 through 11 as Tables 7 through 13;
3. Revising paragraph (b) and the introductory text of paragraph (c);
4. In paragraph (d)(1) introductory text, removing "Table 7" and adding in its place "Table 9";
5. In paragraph (d)(2) introductory text, removing "Table 8" and adding in its place "Table 10"; and
6. In paragraph (d)(3) introductory text, removing "Table 9" and adding in its place "Table 11".

The revisions read as follows:

1. **ndards and their compliance dates.**

\*    \*    \*    \*    \*

1. Each commercial air conditioner or heat pump (not including single package vertical air conditioners and single package vertical heat pumps, packaged terminal air conditioners and packaged terminal heat pumps, computer room air conditioners, and variable refrigerant flow systems) manufactured starting on the compliance date listed in the corresponding table must meet the applicable minimum energy efficiency standard level(s) set forth in Tables 1 through 6 of this section.

| **Table 1 to § 431.97--Minimum Cooling Efficiency Standards for Air** | | | | | |
| --- | --- | --- | --- | --- | --- |
| **Conditioning and Heating Equipment** | | | | | |
| **[Not including single package vertical air conditioners and single package** | | | | | |
| **vertical heat pumps, packaged terminal air conditioners and packaged** | | | | | |
| **terminal heat pumps, computer room air conditioners, and variable** | | | | | |
| **refrigerant flow multi-split air conditioners and heat pumps]** | | | | | |
|  |  |  |  |  |  |
| **Equipment** | **Cooling** | **Sub-category** | **Heating type** | **Efficiency** | **Compliance** |
| **type** | **capacity** |  |  | **level** | **date:** |
|  |  |  |  |  | **Equipment** |
|  |  |  |  |  | **manufactured** |
|  |  |  |  |  | **starting on** |
|  |  |  |  |  | **. . .** |
| Small | <65,000 | AC | All | SEER = 13 | June 16, |
| Commercial | Btu/h |  |  |  | 2008. |
| Package Air |  |  |  |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled, |  |  |  |  |  |
| 3-Phase, |  |  |  |  |  |
| Split- |  |  |  |  |  |
| System) |  |  |  |  |  |
|  |  | HP | All | SEER = 13 | June 16, |
|  |  |  |  |  | 2008. fn1 |
| Small | <65,000 | AC | All | SEER = 13 | June 16, |
| Commercial | Btu/h |  |  |  | 2008. fn1 |
| Package Air |  |  |  |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled, |  |  |  |  |  |
| 3-Phase, |  |  |  |  |  |
| Single- |  |  |  |  |  |
| Package) |  |  |  |  |  |
|  |  | HP | All | SEER = 13 | June 16, |
|  |  |  |  |  | 2008. fn1 |
| Small | >/=65,000 | AC | No Heating | EER = 11.2 | January 1, |
| Commercial | Btu/h and |  | or Electric |  | 2010. fn2 |
| Package Air | <135,000 |  | Resistance |  |  |
| Conditioning | Btu/h |  | Heating |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 11.0 | January 1, |
|  |  |  | Types of |  | 2010. fn2 |
|  |  |  | Heating |  |  |
|  |  | HP | No Heating | EER = 11.0 | January 1, |
|  |  |  | or Electric |  | 2010. fn2 |
|  |  |  | Resistance |  |  |
|  |  |  | Heating |  |  |
|  |  |  | All Other | EER = 10.8 | January 1, |
|  |  |  | Types of |  | 2010. fn2 |
|  |  |  | Heating |  |  |
| Large | >/=135,000 | AC | No Heating | EER = 11.0 | January 1, |
| Commercial | Btu/h and |  | or Electric |  | 2010. fn2 |
| Package Air | <240,000 |  | Resistance |  |  |
| Conditioning | Btu/h |  | Heating |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 10.8 | January 1, |
|  |  |  | Types of |  | 2010. fn2 |
|  |  |  | Heating |  |  |
|  |  | HP | No Heating | EER = 10.6 | January 1, |
|  |  |  | or Electric |  | 2010. fn2 |
|  |  |  | Resistance |  |  |
|  |  |  | Heating |  |  |
|  |  |  | All Other | EER = 10.4 | January 1, |
|  |  |  | Types of |  | 2010. fn2 |
|  |  |  | Heating |  |  |
| Very Large | >/=240,000 | AC | No Heating | EER = 10.0 | January 1, |
| Commercial | Btu/h and |  | or Electric |  | 2010. fn2 |
| Package Air | <760,000 |  | Resistance |  |  |
| Conditioning | Btu/h |  | Heating |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 9.8 | January 1, |
|  |  |  | Types of |  | 2010. fn2 |
|  |  |  | Heating |  |  |
|  |  | HP | No Heating | EER = 9.5 | January 1, |
|  |  |  | or Electric |  | 2010. fn2 |
|  |  |  | Resistance |  |  |
|  |  |  | Heating |  |  |
|  |  |  | All Other | EER = 9.3 | January 1, |
|  |  |  | Types of |  | 2010. fn2 |
|  |  |  | Heating |  |  |
| Small | <65,000 | AC | All | EER = 12.1 | October 29, |
| Commercial | Btu/h |  |  |  | 2003. |
| Package Air |  |  |  |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Water- |  |  |  |  |  |
| Cooled) |  |  |  |  |  |
|  | >/=65,000 | AC | No Heating | EER = 12.1 | June 1, |
|  | Btu/h and |  | or Electric |  | 2013. |
|  | <135,000 |  | Resistance |  |  |
|  | Btu/h |  | Heating |  |  |
|  |  |  | All Other | EER = 11.9 | June 1, |
|  |  |  | Types of |  | 2013. |
|  |  |  | Heating |  |  |
| Large | >/=135,000 | AC | No Heating | EER = 12.5 | June 1, |
| Commercial | Btu/h and |  | or Electric |  | 2014. |
| Package Air- | <240,000 |  | Resistance |  |  |
| Conditioning | Btu/h |  | Heating |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Water- |  |  |  |  |  |
| Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 12.3 | June 1, |
|  |  |  | Types of |  | 2014. |
|  |  |  | Heating |  |  |
| Very Large | >/=240,000 | AC | No Heating | EER = 12.4 | June 1, |
| Commercial | Btu/h and |  | or Electric |  | 2014. |
| Package Air- | <760,000 |  | Resistance |  |  |
| Conditioning | Btu/h |  | Heating |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Water- |  |  |  |  |  |
| Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 12.2 | June 1, |
|  |  |  | Types of |  | 2014. |
|  |  |  | Heating |  |  |
| Small | <65,000 | AC | All | EER = 12.1 | October 29, |
| Commercial | Btu/h |  |  |  | 2003. |
| Package Air- |  |  |  |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Evaporative |  |  |  |  |  |
| ly-Cooled) |  |  |  |  |  |
|  | >/=65,000 | AC | No Heating | EER = 12.1 | June 1, |
|  | Btu/h and |  | or Electric |  | 2013. |
|  | <135,000 |  | Resistance |  |  |
|  | Btu/h |  | Heating |  |  |
|  |  |  | All Other | EER = 11.9 | June 1, |
|  |  |  | Types of |  | 2013. |
|  |  |  | Heating |  |  |
| Large | >/=135,000 | AC | No Heating | EER = 12.0 | June 1, |
| Commercial | Btu/h and |  | or Electric |  | 2014. |
| Package Air- | <240,000 |  | Resistance |  |  |
| Conditioning | Btu/h |  | Heating |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Evaporative |  |  |  |  |  |
| ly-Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 11.8 | June 1, |
|  |  |  | Types of |  | 2014. |
|  |  |  | Heating |  |  |
| Very Large | >/=240,000 | AC | No Heating | EER = 11.9 | June 1, |
| Commercial | Btu/h and |  | or Electric |  | 2014. |
| Package Air | <760,000 |  | Resistance |  |  |
| Conditioning | Btu/h |  | Heating |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Evaporative |  |  |  |  |  |
| ly-Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 11.7 | June 1, |
|  |  |  | Types of |  | 2014. |
|  |  |  | Heating |  |  |
| Small | <17,000 | HP | All | EER = 11.2 | October 29, |
| Commercial | Btu/h |  |  |  | 2003. fn3 |
| Package Air- |  |  |  |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Water- |  |  |  |  |  |
| Source: |  |  |  |  |  |
| Water-to- |  |  |  |  |  |
| Air, Water- |  |  |  |  |  |
| Loop) |  |  |  |  |  |
|  | >/=17,000 | HP | All | EER = 12.0 | October 29, |
|  | Btu/h and |  |  |  | 2003. fn3 |
|  | <65,000 |  |  |  |  |
|  | Btu/h |  |  |  |  |
|  | >/=65,000 | HP | All | EER = 12.0 | October 29, |
|  | Btu/h and |  |  |  | 2003. fn3 |
|  | <135,000 |  |  |  |  |
|  | Btu/h |  |  |  |  |

**fn1** And manufactured before January 1, 2017. See Table 3 of this section for updated efficiency standards.

**fn2** And manufactured before January 1, 2018. See Table 3 of this section for updated efficiency standards.

**fn3** And manufactured before October 9, 2015. See Table 3 of this section for updated efficiency standards.

| **Table 2 to § 431.97--Minimum Heating Efficiency Standards for Air** | | | |
| --- | --- | --- | --- |
| **Conditioning and Heating Equipment** | | | |
| **[Heat pumps]** | | | |
| **[Not including single package vertical air conditioners and single package** | | | |
| **vertical heat pumps, packaged terminal air conditioners and packaged terminal** | | | |
| **heat pumps, computer room air conditioners, variable refrigerant flow** | | | |
| **multi-split air conditioners and heat pumps, and double-duct air-cooled** | | | |
| **commercial package air conditioning and heating equipment]** | | | |
|  |  |  |  |
| **Equipment type** | **Cooling capacity** | **Efficiency level** | **Compliance date:** |
|  |  |  | **Equipment** |
|  |  |  | **manufactured** |
|  |  |  | **starting on . .** |
|  |  |  | **.** |
| Small Commercial | <65,000 Btu/h | HSPF = 7.7 | June 16, 2008. |
| Package Air |  |  | fn1 |
| Conditioning and |  |  |  |
| Heating Equipment |  |  |  |
| (Air-Cooled, 3-Phase, |  |  |  |
| Split-System) |  |  |  |
| Small Commercial | <65,000 Btu/h | HSPF = 7.7 | June 16, 2008. |
| Package |  |  | fn1 |
| Air-Conditioning and |  |  |  |
| Heating Equipment |  |  |  |
| (Air-Cooled, 3-Phase, |  |  |  |
| Single-Package) |  |  |  |
| Small Commercial | >/= 65,000 Btu/h | COP = 3.3 | January 1, 2010. |
| Package Air | and <135,000 |  | fn2 |
| Conditioning and | Btu/h |  |  |
| Heating Equipment |  |  |  |
| (Air-Cooled) |  |  |  |
| Large Commercial | >/= 135,000 | COP = 3.2 | January 1, 2010. |
| Packaged Air | Btu/h and |  | fn2 |
| Conditioning and | <240,000 Btu/h |  |  |
| Heating Equipment |  |  |  |
| (Air-Cooled) |  |  |  |
| Very Large Commercial | >/= 240,000 | COP = 3.2 | January 1, 2010. |
| Packaged Air | Btu/h and |  | fn2 |
| Conditioning and | <760,000 Btu/h |  |  |
| Heating Equipment |  |  |  |
| (Air-Cooled) |  |  |  |
| Small Commercial | <135,000 Btu/h | COP = 4.2 | October 29, |
| Packaged Air |  |  | 2003. |
| Conditioning and |  |  |  |
| Heating Equipment |  |  |  |
| (Water-Source: |  |  |  |
| Water-to-Air, |  |  |  |
| Water-Loop) |  |  |  |

**fn1** And manufactured before January 1, 2017. See Table 4 of this section for updated heating efficiency standards.

**fn2** And manufactured before January 1, 2018. See Table 4 of this section for updated heating efficiency standards.

| **Table 3 to § 431.97--Updates to the Minimum Cooling Efficiency Standards** | | | | | |
| --- | --- | --- | --- | --- | --- |
| **for Air Conditioning and Heating Equipment** | | | | | |
| **[Not including single package vertical air conditioners and single package** | | | | | |
| **vertical heat pumps, packaged terminal air conditioners and packaged** | | | | | |
| **terminal heat pumps, computer room air conditioners, variable refrigerant** | | | | | |
| **flow multi-split air conditioners and heat pumps, and double-duct air-cooled** | | | | | |
| **commercial package air conditioning and heating equipment]** | | | | | |
|  |  |  |  |  |  |
| **Equipment** | **Cooling** | **Sub-category** | **Heating type** | **Efficiency** | **Compliance** |
| **type** | **capacity** |  |  | **level** | **date:** |
|  |  |  |  |  | **Equipment** |
|  |  |  |  |  | **manufactured** |
|  |  |  |  |  | **starting on** |
|  |  |  |  |  | **. . .** |
| Small | >/=65,000 | AC | Electric | IEER = 12.9 | January 1, |
| Commercial | Btu/h and |  | Resistance | IEER = 14.8 | 2018. fn1 |
| Packaged Air | <135,000 |  | Heating or |  | January 1, |
| Conditioning | Btu/h |  | No Heating |  | 2023. |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | IEER = 12.7 | January 1, |
|  |  |  | Types of | IEER = 14.6 | 2018. fn1 |
|  |  |  | Heating |  | January 1, |
|  |  |  |  |  | 2023. |
|  |  | HP | Electric | IEER = 12.2 | January 1, |
|  |  |  | Resistance | IEER = 14.1 | 2018. fn1 |
|  |  |  | Heating or |  | January 1, |
|  |  |  | No Heating |  | 2023. |
|  |  |  | All Other | IEER = 12.0 | January 1, |
|  |  |  | Types of | IEER = 13.9 | 2018. fn1 |
|  |  |  | Heating |  | January 1, |
|  |  |  |  |  | 2023. |
| Large | >/=135,000 | AC | Electric | IEER = 12.4 | January 1, |
| Commercial | Btu/h and |  | Resistance | IEER = 14.2 | 2018. fn1 |
| Packaged Air | <240,000 |  | Heating or |  | January 1, |
| Conditioning | Btu/h |  | No Heating |  | 2023. |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | IEER = 12.2 | January 1, |
|  |  |  | Types of | IEER = 14.0 | 2018. fn1 |
|  |  |  | Heating |  | January 1, |
|  |  |  |  |  | 2023. |
|  |  | HP | Electric | IEER = 11.6 | January 1, |
|  |  |  | Resistance | IEER = 13.5 | 2018. fn1 |
|  |  |  | Heating or |  | January 1, |
|  |  |  | No Heating |  | 2023. |
|  |  |  | All Other | IEER = 11.4 | January 1, |
|  |  |  | Types of | IEER = 13.3 | 2018. fn1 |
|  |  |  | Heating |  | January 1, |
|  |  |  |  |  | 2023. |
| Very Large | >/=240,000 | AC | Electric | IEER = 11.6 | January 1, |
| Commercial | Btu/h and |  | Resistance | IEER = 13.2 | 2018. fn1 |
| Packaged Air | <760,000 |  | Heating or |  | January 1, |
| Conditioning | Btu/h |  | No Heating |  | 2023. |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | IEER = 11.4 | January 1, |
|  |  |  | Types of | IEER = 13.0 | 2018. fn1 |
|  |  |  | Heating |  | January 1, |
|  |  |  |  |  | 2023. |
|  |  | HP | Electric | IEER = 10.6 | January 1, |
|  |  |  | Resistance | IEER = 12.5 | 2018. fn1 |
|  |  |  | Heating or |  | January 1, |
|  |  |  | No Heating |  | 2023. |
|  |  |  | All Other | IEER = 10.4 | January 1, |
|  |  |  | Types of | IEER = 12.3 | 2018. fn1 |
|  |  |  | Heating |  | January 1, |
|  |  |  |  |  | 2023. |
| Small | <65,000 | AC | All | SEER = 13.0 | June 16, |
| Commercial | Btu/h |  |  |  | 2008. |
| Package Air- |  |  |  |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled, |  |  |  |  |  |
| 3-Phase, |  |  |  |  |  |
| Split- |  |  |  |  |  |
| System) |  |  |  |  |  |
|  |  | HP | All | SEER = 14.0 | January 1, |
|  |  |  |  |  | 2017. |
| Small | <65,000 | AC | All | SEER = 14.0 | January 1, |
| Commercial | Btu/h |  |  |  | 2017. |
| Package Air- |  |  |  |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled, |  |  |  |  |  |
| 3-Phase, |  |  |  |  |  |
| Single- |  |  |  |  |  |
| Package) |  |  |  |  |  |
|  |  | HP | All | SEER = 14.0 | January 1, |
|  |  |  |  |  | 2017. |
| Small | <17,000 | HP | All | EER = 12.2 | October 9, |
| Commercial | Btu/h |  |  |  | 2015. |
| Packaged |  |  |  |  |  |
| Air- |  |  |  |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Water |  |  |  |  |  |
| Source: |  |  |  |  |  |
| Water-to- |  |  |  |  |  |
| Air, Water- |  |  |  |  |  |
| Loop) |  |  |  |  |  |
|  | >/=17,000 | HP | All | EER = 13.0 | October 9, |
|  | Btu/h and |  |  |  | 2015. |
|  | <65,000 |  |  |  |  |
|  | Btu/h |  |  |  |  |
|  | >/=65,000 | HP | All | EER = 13.0 | October 9, |
|  | Btu/h and |  |  |  | 2015. |
|  | <135,000 |  |  |  |  |
|  | Btu/h |  |  |  |  |

**fn1** And manufactured before January 1, 2023.

| **Table 4 to § 431.97--Updates to the Minimum Heating Efficiency Standards for** | | | |
| --- | --- | --- | --- |
| **Air-Cooled Air Conditioning and Heating Equipment** | | | |
| **[Heat Pumps]** | | | |
| **[Not including single package vertical air conditioners and single package** | | | |
| **vertical heat pumps, packaged terminal air conditioners and packaged terminal** | | | |
| **heat pumps, computer room air conditioners, variable refrigerant flow** | | | |
| **multi-split air conditioners and heat pumps, and double-duct air-cooled** | | | |
| **commercial package air conditioning and heating equipment]** | | | |
|  |  |  |  |
| **Equipment type** | **Cooling capacity** | **Efficiency** | **Compliance** |
|  |  | **level fn1** | **date:** |
|  |  |  | **equipment** |
|  |  |  | **manufactured** |
|  |  |  | **starting on .** |
|  |  |  | **. .** |
| Small Commercial Package Air | <65,000 Btu/h | HSPF = 8.2 | January 1, |
| Conditioning and Heating |  |  | 2017. |
| Equipment (Air-Cooled, |  |  |  |
| 3-Phase, Split-Sytem) |  |  |  |
| Small Commercial Package Air | <65,000 Btu/h | HSPF = 8.0 | January 1, |
| Conditioning and Heating |  |  | 2017. |
| Equipment (Air-Cooled, |  |  |  |
| 3-Phase, Single Package) |  |  |  |
| Small Commercial Package Air | <135,000 Btu/h | COP = 4.3 | October 9, |
| Conditioning and Heating |  |  | 2015. |
| Equipment (Water-Source: |  |  |  |
| Water-to-Air, Water-Loop) |  |  |  |
| Small Commercial Packaged Air | >/= 65,000 Btu/h | COP = 3.3 | January 1, |
| Conditioning and Heating | and <135,000 | COP = 3.4 | 2018. fn2 . |
| Equipment (Air-Cooled) | Btu/h |  | January 1, |
|  |  |  | 2023. |
| Large Commercial Packaged Air | >/= 135,000 | COP = 3.2 | January 1, |
| Conditioning and Heating | Btu/h and | COP = 3.3 | 2018. fn2 . |
| Equipment (Air-Cooled) | <240,000 Btu/h |  | January 1, |
|  |  |  | 2023. |
| Very Large Commercial Packaged | >/= 240,000 | COP = 3.2 | January 1, |
| Air Conditioning and Heating | Btu/h and |  | 2018. |
| Equipment (Air-Cooled) | <760,000 Btu/h |  |  |

**fn1** For units tested using the relevant AHRI Standards, all COP values must be rated at 47&emsp14; [degrees] F outdoor dry-bulb temperature for air-cooled equipment.

**fn2** And manufactured before January 1, 2023. **[\*2129]**

| **Table 5 to § 431.97--Minimum Cooling Efficiency Standards for Double-Duct** | | | | | |
| --- | --- | --- | --- | --- | --- |
| **Air-Conditioning and Heating Equipment** | | | | | |
|  |  |  |  |  |  |
| **Equipment** | **Cooling** | **Sub-category** | **Heating type** | **Efficiency** | **Compliance** |
| **type** | **capacity** |  |  | **level** | **date:** |
|  |  |  |  |  | **equipment** |
|  |  |  |  |  | **manufactured** |
|  |  |  |  |  | **starting on.** |
|  |  |  |  |  | **. .** |
| Small | >/= 65,000 | AC | Electric | EER = 11.2 | January 1, |
| Double-Duct | Btu/h and |  | Resistance |  | 2010. |
| Commercial | <135,000 |  | Heating or |  |  |
| Packaged Air | Btu/h |  | No Heating |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 11.0 | January 1, |
|  |  |  | Types of |  | 2010. |
|  |  |  | Heating |  |  |
|  |  | HP | Electric | EER = 11.0 | January 1, |
|  |  |  | Resistance |  | 2010. |
|  |  |  | Heating or |  |  |
|  |  |  | No Heating |  |  |
|  |  |  | All Other | EER = 10.8 | January 1, |
|  |  |  | Types of |  | 2010. |
|  |  |  | Heating |  |  |
| Large | >/= 135,000 | AC | Electric | EER = 11.0 | January 1, |
| Commercial | Btu/h and |  | Resistance |  | 2010. |
| Double-Duct | <240,000 |  | Heating or |  |  |
| Packaged Air | Btu/h |  | No Heating |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 10.8 | January 1, |
|  |  |  | Types of |  | 2010. |
|  |  |  | Heating |  |  |
|  |  | HP | Electric | EER = 10.6 | January 1, |
|  |  |  | Resistance |  | 2010. |
|  |  |  | Heating or |  |  |
|  |  |  | No Heating |  |  |
|  |  |  | All Other | EER = 10.4 | January 1, |
|  |  |  | Types of |  | 2010. |
|  |  |  | Heating |  |  |
| Very Large | >/= 240,000 | AC | Electric | EER = 10.0 | January 1, |
| Double-Duct | Btu/h and |  | Resistance |  | 2010. |
| Commercial | <300,000 |  | Heating or |  |  |
| Packaged Air | Btu/h |  | No Heating |  |  |
| Conditioning |  |  |  |  |  |
| and Heating |  |  |  |  |  |
| Equipment |  |  |  |  |  |
| (Air-Cooled) |  |  |  |  |  |
|  |  |  | All Other | EER = 9.8 | January 1, |
|  |  |  | Types of |  | 2010. |
|  |  |  | Heating |  |  |
|  |  | HP | Electric | EER = 9.5 | January 1, |
|  |  |  | Resistance |  | 2010. |
|  |  |  | Heating or |  |  |
|  |  |  | No Heating |  |  |
|  |  |  | All Other | EER = 9.3 | January 1, |
|  |  |  | Types of |  | 2010. |
|  |  |  | Heating |  |  |

| **Table 6 to § 431.97--Minimum Heating Efficiency Standards for Double-Duct** | | | | |
| --- | --- | --- | --- | --- |
| **Air-Cooled Air Conditioning and Heating Equipment** | | | | |
| **[Heat pumps]** | | | | |
|  |  |  |  |  |
| **Equipment type** | **Cooling** | **Heating type** | **Efficiency** | **Compliance** |
|  | **capacity** |  | **level fn1** | **date:** |
|  |  |  |  | **Equipment** |
|  |  |  |  | **manufactured** |
|  |  |  |  | **starting on…** |
| Small | >/=65,000 | Electric | COP = 3.3 | January 1, |
| Commercial | Btu/h and | Resistance |  | 2010. |
| Packaged Air | <135,000 Btu/h | Heating or No |  |  |
| Conditioning |  | Heating |  |  |
| and Heating |  |  |  |  |
| Equipment |  |  |  |  |
| (Air-Cooled) |  |  |  |  |
|  |  | All Other | COP = 3.3 | January 1, |
|  |  | Types of |  | 2010. |
|  |  | Heating |  |  |
| Large | >/=135,000 | Electric | COP = 3.2 | January 1, |
| Commercial | Btu/h and | Resistance |  | 2010. |
| Packaged Air- | <240,000 Btu/h | Heating or No |  |  |
| Conditioning |  | Heating |  |  |
| and Heating |  |  |  |  |
| Equipment |  |  |  |  |
| (Air-Cooled) |  |  |  |  |
|  |  | All Other | COP = 3.2 | January 1, |
|  |  | Types of |  | 2010. |
|  |  | Heating |  |  |
| Very Large | >/=240,000 | Electric | COP = 3.2 | January 1, |
| Commercial | Btu/h and | Resistance |  | 2010. |
| Packaged Air | <300,000 Btu/h | Heating or No |  |  |
| Conditioning |  | Heating |  |  |
| and Heating |  |  |  |  |
| Equipment |  |  |  |  |
| (Air-Cooled) |  |  |  |  |
|  |  | All Other | COP = 3.2 | January 1, |
|  |  | Types of |  | 2010. |
|  |  | Heating |  |  |

**fn1** For units tested using the relevant AHRI Standards, all COP values must be rated at 47 [degrees] F outdoor dry-bulb temperature for air-cooled equipment.

1. Each packaged terminal air conditioner (PTAC) and packaged terminal heat pump (PTHP) manufactured starting on January 1, 1994, but before October 8, 2012 (for standard size PTACs and PTHPs) and before October 7, 2010 (for non-standard size PTACs and PTHPs) must meet the applicable minimum energy efficiency standard level(s) set forth in Table 7 of this section. Each standard size PTAC and PTHP manufactured starting on October 8, 2012, and each non-standard size PTAC and PTHP manufactured starting on October 7, 2010, must meet the applicable minimum energy efficiency standard level(s) set forth in Table 6 of this section.

   \*    \*    \*    \*    \*

[FR Doc. 2015-33069 Filed 1-14-16; 8:45 am]

BILLING CODE 6450-01-P

**Dates**

**DATES:** DOE will accept comments, data, and information regarding the proposed standards no later than May 4, 2016.

Comments regarding the likely ***competitive*** impact of the proposed standard should be sent to the Department of Justice contact listed in the **ADDRESSES** section before February 16, 2016.

**Contacts**

**ADDRESSES:** *Instructions:* Any comments submitted must identify the proposed rule for Energy Conservation Standards for small, large, and very large air-cooled commercial package air conditioning and heating equipment (CUACs and CUHPs) and commercial warm air furnaces (CWAFs), and provide docket number EERE-2013-BT-STD-0007 and/or regulatory information number (RIN) 1904-AC95 for CUACs and CUHPs and EERE-2013-BT-STD-0021 and/or RIN 1904-AD11 for CWAFs. Comments may be submitted using any of the following methods:

1. *Federal eRulemaking Portal:* [*www.****regulations****.gov*](http://www.regulations.gov)*.* Follow the instructions for submitting comments.

2. *Email:* For CUACs and CUHPs: [*CommPkgACHP2013STD0007@ee.doe.gov*](mailto:CommPkgACHP2013STD0007@ee.doe.gov). For CWAFs: [*CommWarmAirFurn2013STD0021@ee.doe.gov*](mailto:CommWarmAirFurn2013STD0021@ee.doe.gov). Include the docket number and/or RIN for each equipment category in the subject line of the message. Submit electronic comments in WordPerfect, Microsoft Word, PDF, or ASCII file format, and avoid the use of special characters or any form of encryption.

3. *Postal Mail:* Ms. Brenda Edwards, U.S. Department of Energy, Building Technologies Office, Mailstop EE-5B, 1000 Independence Avenue SW., Washington, DC 20585-0121. If possible, please submit all items on a compact disc (CD), in which case it is not necessary to include printed copies.

4. *Hand Delivery/Courier:* Ms. Brenda Edwards, U.S. Department of Energy, Building Technologies Office, 950 L'Enfant Plaza SW., Room 6094, Washington, DC 20024. Telephone: (202) 586-2945. If possible, please submit all items on a CD, in which case it is not necessary to include printed copies.

No telefacsimilies (faxes) will be accepted.

For detailed instructions on submitting comments and additional information on the rulemaking process, see section III of this document ("Public Participation").

Written comments regarding the burden-hour estimates or other aspects of the collection-of-information requirements contained in this proposed rule may be submitted to Office of Energy Efficiency and Renewable Energy through the methods listed above and by email to [*Chad\_S\_Whiteman@omb.eop.gov*](mailto:Chad_S_Whiteman@omb.eop.gov)*.*

EPCA requires the Attorney General to provide DOE a written determination of whether the proposed standard is likely to lessen ***competition***. The U.S. Department of Justice ***Antitrust*** Division invites input from market participants and other interested persons with views on the likely ***competitive*** impact of the proposed standard. Interested persons may contact the Division at [*energy.standards@atr.usdoj.gov*](mailto:energy.standards@atr.usdoj.gov) before February 16, 2016. Please indicate in the "Subject" line of your email the title and Docket Number of this rulemaking notice.

**Federal Register** notices, public meeting attendee lists and transcripts, comments, and other supporting documents/materials, is available for review at [*www.****regulations****.gov*](http://www.regulations.gov)*.* All documents in the dockets are listed in the [*www.****regulations****.gov*](http://www.regulations.gov) index. However, some documents listed in the index, such as those containing information that is exempt from public disclosure, may not be publicly available.

A link to the docket Web page for small, large, and very large air-cooled commercial package air conditioning and heating equipment can be found at: [*www.****regulations****.gov/#!docketDetail*](http://www.regulations.gov/#!docketDetail)*;D=EERE-2013-BT-STD-0007.* A link to the docket Web page for commercial warm air furnaces can be found at: [*www.****regulations****.gov/#!docketDetail*](http://www.regulations.gov/#!docketDetail)*;D=EERE-2013-BT-STD-0021.* The [*www.****regulations****.gov*](http://www.regulations.gov) Web page will contain instructions on how to access all documents, including public comments, in the docket.

For further information on how to review the dockets, please contact Ms. Brenda Edwards at (202) 586-2945 or by email: [*Brenda.Edwards@ee.doe.gov*](mailto:Brenda.Edwards@ee.doe.gov)*.* **[\*2112]**

**FOR FURTHER INFORMATION CONTACT:** Mr. John Cymbalsky, U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy, Building Technologies, EE-5B, 1000 Independence Avenue SW., Washington, DC 20585-0121. Telephone: (202) 286-1692. Email: [*John.Cymbalsky@ee.doe.gov*](mailto:John.Cymbalsky@ee.doe.gov)*.*

FEDERAL REGISTER

**End of Document**